## 0900CIEB
0900CIEB — Tubular Centrifugal Inline Fan (TCLB / TCLBR)
Wheel Dia. 10.50" • Outlet Dia. 16.13" • Outlet Area 1.42 ft² • Tip Speed FPM = 2.75 × RPM • Max BHP = 0.022 × (RPM÷1000)³ • —
Maximum RPM: Level 1 (A1) = 2728, Level 2 (A2) = 3637 ¦ Maximum Motor Frame: Level 1 (A1) = 56, Level 2 (A2) = 145T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
250 | 176 | 850 | 0.01 | 2.8 | 1024 | 0.02 | 4.1 | 1320 | 0.05 | 6.4 | 1792 | 0.1 | 10 | 2176 | 0.16 | 12.5
330 | 233 | 1011 | 0.02 | 4.3 | 1157 | 0.03 | 5.2 | 1415 | 0.06 | 7 | 1844 | 0.12 | 10.6 | 2206 | 0.19 | 13.5 | 2526 | 0.27 | 15.8 | 2811 | 0.35 | 17.4 | 3070 | 0.44 | 19.4
410 | 289 | 1183 | 0.04 | 5.9 | 1313 | 0.05 | 6.6 | 1537 | 0.08 | 8 | 1927 | 0.15 | 11.3 | 2264 | 0.22 | 14.3 | 2564 | 0.31 | 16.7 | 2840 | 0.4 | 18.4 | 3095 | 0.5 | 21 | 3332 | 0.6 | 22 | 3554 | 0.71 | 23
490 | 346 | 1364 | 0.05 | 7.1 | 1479 | 0.07 | 8.1 | 1680 | 0.1 | 9.1 | 2034 | 0.18 | 12.2 | 2346 | 0.26 | 14.9 | 2630 | 0.35 | 17.1 | 2890 | 0.45 | 19.4 | 3133 | 0.55 | 21 | 3362 | 0.66 | 23 | 3580 | 0.78 | 25
570 | 402 | 1549 | 0.08 | 8.7 | 1652 | 0.1 | 9.9 | 1837 | 0.13 | 10.8 | 2158 | 0.22 | 13.4 | 2448 | 0.31 | 15.5 | 2714 | 0.41 | 17.8 | 2962 | 0.51 | 20 | 3193 | 0.62 | 22 | 3412 | 0.73 | 24 | 3620 | 0.85 | 26
650 | 458 | 1739 | 0.11 | 10.3 | 1831 | 0.13 | 11 | 2001 | 0.17 | 12.8 | 2297 | 0.26 | 14.4 | 2566 | 0.36 | 16.8 | 2816 | 0.47 | 18.5 | 3050 | 0.58 | 21 | 3271 | 0.7 | 23 | 3480 | 0.82 | 25
730 | 515 | 1931 | 0.15 | 12 | 2014 | 0.17 | 12.8 | 2170 | 0.22 | 14.4 | 2448 | 0.32 | 15.8 | 2696 | 0.42 | 17.9 | 2931 | 0.54 | 19.5 | 3152 | 0.65 | 22 | 3363 | 0.78 | 23 | 3563 | 0.92 | 26
810 | 571 | 2124 | 0.19 | 13.6 | 2200 | 0.22 | 14.3 | 2344 | 0.27 | 16.3 | 2606 | 0.38 | 17.7 | 2838 | 0.5 | 19.4 | 3058 | 0.62 | 22 | 3268 | 0.74 | 23 | 3467 | 0.87 | 25
890 | 628 | 2320 | 0.25 | 15.5 | 2389 | 0.28 | 16.2 | 2523 | 0.34 | 17.9 | 2769 | 0.46 | 19.9 | 2990 | 0.58 | 20 | 3195 | 0.71 | 23 | 3393 | 0.84 | 24 | 3584 | 0.98 | 26
970 | 684 | 2516 | 0.32 | 17.3 | 2580 | 0.35 | 18.2 | 2704 | 0.41 | 19.6 | 2936 | 0.54 | 22 | 3148 | 0.67 | 23 | 3342 | 0.81 | 24 | 3528 | 0.95 | 26
1050 | 740 | 2713 | 0.4 | 19.6 | 2773 | 0.43 | 19.8 | 2889 | 0.5 | 21 | 3107 | 0.64 | 24 | 3309 | 0.78 | 26 | 3496 | 0.92 | 26
1130 | 797 | 2911 | 0.49 | 21 | 2967 | 0.52 | 23 | 3075 | 0.6 | 24 | 3281 | 0.75 | 26 | 3474 | 0.9 | 28
1210 | 853 | 3109 | 0.59 | 24 | 3162 | 0.63 | 24 | 3264 | 0.71 | 26 | 3459 | 0.88 | 29
1290 | 910 | 3308 | 0.71 | 26 | 3357 | 0.75 | 27 | 3454 | 0.84 | 27
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 1050CIEB
1050CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 10.50" • Outlet Dia. 16.13" • Outlet Area 1.42 ft² • Tip Speed FPM = 2.75 × RPM • Max BHP = 0.034 × (RPM÷1000)³ • FEG 60 (size 105A2 only)
Maximum RPM: Level 1 (A1) = 2728, Level 2 (A2) = 3637 ¦ Maximum Motor Frame: Level 1 (A1) = 143T, Level 2 (A2) = 184T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
400 | 282 | 869 | 0.02 | 3.6 | 1031 | 0.04 | 4.6 | 1295 | 0.07 | 6.5 | 1745 | 0.14 | 9.8
520 | 366 | 1038 | 0.04 | 5.5 | 1170 | 0.05 | 6.3 | 1407 | 0.09 | 7.6 | 1799 | 0.17 | 10.8 | 2146 | 0.27 | 13.4 | 2466 | 0.38 | 15.3
640 | 451 | 1221 | 0.06 | 7.1 | 1330 | 0.08 | 8.5 | 1543 | 0.12 | 9.1 | 1894 | 0.22 | 11.5 | 2205 | 0.32 | 14.2 | 2493 | 0.44 | 16.3 | 2761 | 0.57 | 18 | 3020 | 0.7 | 20
760 | 535 | 1411 | 0.09 | 8.8 | 1504 | 0.11 | 10 | 1686 | 0.16 | 11 | 2017 | 0.27 | 13 | 2298 | 0.38 | 14.9 | 2561 | 0.51 | 17 | 2808 | 0.65 | 19 | 3043 | 0.79 | 21 | 3268 | 0.95 | 23 | 3487 | 1.1 | 25
880 | 620 | 1606 | 0.13 | 10.9 | 1687 | 0.16 | 11.8 | 1846 | 0.21 | 13.4 | 2153 | 0.33 | 14.8 | 2414 | 0.46 | 16.1 | 2656 | 0.59 | 17.9 | 2884 | 0.74 | 19.7 | 3103 | 0.89 | 22 | 3313 | 1.05 | 24 | 3515 | 1.22 | 26
1000 | 704 | 1804 | 0.19 | 13.1 | 1876 | 0.21 | 14.1 | 2017 | 0.27 | 15.7 | 2292 | 0.4 | 16.6 | 2548 | 0.54 | 18 | 2771 | 0.69 | 19 | 2983 | 0.84 | 20 | 3187 | 1 | 23 | 3384 | 1.17 | 25 | 3574 | 1.35 | 27
1120 | 789 | 2003 | 0.25 | 15.1 | 2068 | 0.28 | 16 | 2195 | 0.35 | 17.8 | 2442 | 0.49 | 19.1 | 2686 | 0.64 | 19.5 | 2903 | 0.8 | 21 | 3100 | 0.96 | 22 | 3291 | 1.13 | 23 | 3475 | 1.31 | 26
1240 | 873 | 2205 | 0.33 | 17.6 | 2263 | 0.37 | 18.3 | 2379 | 0.44 | 19.7 | 2604 | 0.59 | 22 | 2826 | 0.75 | 21 | 3040 | 0.93 | 23 | 3232 | 1.1 | 24 | 3410 | 1.28 | 26 | 3583 | 1.47 | 26
1360 | 958 | 2407 | 0.43 | 19.9 | 2461 | 0.47 | 20 | 2567 | 0.55 | 21 | 2774 | 0.71 | 24 | 2976 | 0.88 | 24 | 3178 | 1.07 | 25 | 3369 | 1.26 | 26 | 3542 | 1.45 | 28
1480 | 1042 | 2610 | 0.55 | 22 | 2660 | 0.59 | 23 | 2758 | 0.68 | 24 | 2949 | 0.85 | 26 | 3136 | 1.03 | 28 | 3322 | 1.23 | 27 | 3506 | 1.43 | 29
1600 | 1127 | 2814 | 0.69 | 25 | 2860 | 0.73 | 25 | 2951 | 0.82 | 26 | 3129 | 1.01 | 29 | 3303 | 1.2 | 31 | 3474 | 1.4 | 31
1720 | 1211 | 3019 | 0.85 | 27 | 3061 | 0.9 | 27 | 3146 | 0.99 | 29 | 3313 | 1.19 | 31 | 3476 | 1.39 | 34 | 3636 | 1.61 | 35
1840 | 1296 | 3224 | 1.03 | 30 | 3263 | 1.08 | 31 | 3343 | 1.19 | 31 | 3499 | 1.39 | 34
1960 | 1380 | 3429 | 1.24 | 33 | 3466 | 1.29 | 33 | 3541 | 1.4 | 35
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 1225CIEB
1225CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 12.25" • Outlet Dia. 18.25" • Outlet Area 1.82 ft² • Tip Speed FPM = 3.21 × RPM • Max BHP = 0.073 × (RPM÷1000)³ • FEG 63 (size 122A2 only)
Maximum RPM: Level 1 (A1) = 2375, Level 2 (A2) = 3167 ¦ Maximum Motor Frame: Level 1 (A1) = 145T, Level 2 (A2) = 184T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
650 | 357 | 798 | 0.04 | 4.4 | 911 | 0.05 | 4.8 | 1123 | 0.1 | 6.3 | 1496 | 0.2 | 9.7
820 | 451 | 951 | 0.06 | 6.1 | 1045 | 0.08 | 6.7 | 1220 | 0.13 | 7.8 | 1545 | 0.25 | 10.3 | 1836 | 0.38 | 13.6
990 | 544 | 1111 | 0.09 | 7.7 | 1191 | 0.12 | 8.7 | 1342 | 0.18 | 9.4 | 1625 | 0.3 | 11.6 | 1886 | 0.45 | 14.7 | 2129 | 0.61 | 16.7 | 2359 | 0.78 | 19
1160 | 637 | 1274 | 0.14 | 9.7 | 1346 | 0.17 | 10.4 | 1477 | 0.23 | 11.7 | 1726 | 0.37 | 13.3 | 1963 | 0.52 | 15 | 2185 | 0.7 | 17.6 | 2395 | 0.88 | 19.9 | 2597 | 1.08 | 22 | 2790 | 1.29 | 23
1330 | 731 | 1441 | 0.2 | 11.5 | 1504 | 0.24 | 12.6 | 1623 | 0.31 | 14 | 1845 | 0.45 | 14.6 | 2057 | 0.62 | 16.9 | 2261 | 0.8 | 18.2 | 2456 | 1 | 20 | 2642 | 1.2 | 22 | 2822 | 1.42 | 24 | 2997 | 1.65 | 25
1500 | 824 | 1609 | 0.28 | 14.1 | 1666 | 0.32 | 14.7 | 1775 | 0.4 | 16.3 | 1975 | 0.56 | 17.6 | 2167 | 0.73 | 18.4 | 2354 | 0.92 | 20 | 2535 | 1.13 | 21 | 2709 | 1.35 | 23 | 2877 | 1.58 | 25 | 3039 | 1.81 | 27
1670 | 918 | 1779 | 0.37 | 16.1 | 1831 | 0.42 | 16.9 | 1930 | 0.51 | 18.8 | 2114 | 0.68 | 20 | 2290 | 0.87 | 20 | 2460 | 1.07 | 22 | 2628 | 1.28 | 23 | 2791 | 1.51 | 24 | 2948 | 1.75 | 25 | 3101 | 2 | 27
1840 | 1011 | 1950 | 0.49 | 18.8 | 1997 | 0.54 | 19 | 2089 | 0.63 | 21 | 2259 | 0.83 | 23 | 2422 | 1.03 | 23 | 2579 | 1.24 | 23 | 2733 | 1.46 | 24 | 2885 | 1.7 | 25 | 3033 | 1.95 | 27
2010 | 1104 | 2121 | 0.63 | 21 | 2165 | 0.68 | 22 | 2250 | 0.79 | 23 | 2410 | 1 | 25 | 2560 | 1.21 | 26 | 2707 | 1.44 | 24 | 2849 | 1.67 | 25 | 2990 | 1.91 | 26 | 3129 | 2.17 | 28
2180 | 1198 | 2293 | 0.79 | 23 | 2334 | 0.85 | 24 | 2413 | 0.96 | 25 | 2563 | 1.19 | 27 | 2704 | 1.42 | 28 | 2841 | 1.66 | 27 | 2975 | 1.91 | 26 | 3106 | 2.16 | 28
2350 | 1291 | 2466 | 0.98 | 26 | 2504 | 1.04 | 26 | 2578 | 1.16 | 27 | 2719 | 1.41 | 30 | 2852 | 1.66 | 30 | 2980 | 1.91 | 30 | 3106 | 2.17 | 29
2520 | 1385 | 2639 | 1.19 | 28 | 2674 | 1.26 | 28 | 2744 | 1.39 | 30 | 2877 | 1.66 | 31 | 3003 | 1.93 | 32 | 3124 | 2.2 | 33
2690 | 1478 | 2812 | 1.44 | 30 | 2846 | 1.51 | 31 | 2911 | 1.66 | 31 | 3037 | 1.94 | 34 | 3157 | 2.23 | 35
2860 | 1571 | 2986 | 1.73 | 32 | 3017 | 1.8 | 32 | 3079 | 1.95 | 34
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 1350CIEB
1350CIEB — Tubular Centrifugal Inline Fan
Still on your side — data imports on the admin Import screen (each once: catalogue then ratings): ceb-7300-ratings.csv — fixes the 73" CEB didw-catalogue.csv + didw-ratings.csv — DIDWCEB (also powers CEBCAB) 1350CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 13.50" • Outlet Dia. 21.25" • Outlet Area 2.46 ft² • Tip Speed FPM = 3.53 × RPM • Max BHP = 0.13 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 2156, Level 2 (A2) = 2874 ¦ Maximum Motor Frame: Level 1 (A1) = 145T, Level 2 (A2) = 215T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
800 | 325 | 685 | 0.04 | 4.8 | 791 | 0.07 | 6 | 989 | 0.12 | 8
1015 | 412 | 815 | 0.07 | 6.4 | 903 | 0.1 | 7.7 | 1066 | 0.16 | 9.3 | 1370 | 0.31 | 13.4
1230 | 499 | 953 | 0.11 | 7.9 | 1027 | 0.14 | 9.5 | 1167 | 0.21 | 11 | 1429 | 0.37 | 14.4 | 1675 | 0.57 | 17.6
1445 | 587 | 1096 | 0.16 | 10.1 | 1159 | 0.2 | 11.1 | 1282 | 0.28 | 13.1 | 1512 | 0.45 | 16.7 | 1730 | 0.66 | 17.9 | 1939 | 0.89 | 20
1660 | 674 | 1241 | 0.23 | 12.3 | 1296 | 0.27 | 13.2 | 1405 | 0.36 | 15.7 | 1611 | 0.55 | 18 | 1806 | 0.77 | 19.2 | 1995 | 1.01 | 20 | 2178 | 1.27 | 23 | 2355 | 1.55 | 24
1875 | 761 | 1388 | 0.32 | 14.4 | 1437 | 0.36 | 15.5 | 1534 | 0.46 | 17.6 | 1722 | 0.67 | 19.5 | 1898 | 0.9 | 21 | 2069 | 1.15 | 22 | 2237 | 1.42 | 23 | 2399 | 1.71 | 24 | 2558 | 2.02 | 27
2090 | 849 | 1537 | 0.43 | 17.4 | 1581 | 0.48 | 17.7 | 1668 | 0.59 | 18.9 | 1840 | 0.81 | 21 | 2001 | 1.06 | 22 | 2158 | 1.32 | 23 | 2311 | 1.6 | 24 | 2462 | 1.9 | 25 | 2609 | 2.22 | 27 | 2753 | 2.55 | 30
2305 | 936 | 1687 | 0.56 | 19.2 | 1726 | 0.62 | 19.9 | 1806 | 0.74 | 21 | 1962 | 0.98 | 24 | 2113 | 1.24 | 23 | 2257 | 1.52 | 24 | 2399 | 1.82 | 25 | 2538 | 2.13 | 27 | 2675 | 2.45 | 29 | 2809 | 2.79 | 31
2520 | 1023 | 1837 | 0.72 | 21 | 1873 | 0.78 | 22 | 1946 | 0.91 | 23 | 2090 | 1.17 | 25 | 2231 | 1.45 | 26 | 2366 | 1.75 | 25 | 2496 | 2.06 | 27 | 2625 | 2.38 | 29 | 2753 | 2.72 | 31
2735 | 1110 | 1987 | 0.91 | 23 | 2021 | 0.98 | 24 | 2088 | 1.11 | 25 | 2221 | 1.4 | 27 | 2353 | 1.69 | 28 | 2480 | 2 | 28 | 2603 | 2.33 | 28 | 2723 | 2.67 | 31 | 2841 | 3.02 | 32
2950 | 1198 | 2138 | 1.13 | 26 | 2170 | 1.2 | 26 | 2232 | 1.35 | 27 | 2355 | 1.65 | 29 | 2478 | 1.97 | 30 | 2598 | 2.29 | 32 | 2715 | 2.63 | 32 | 2828 | 2.99 | 32
3165 | 1285 | 2290 | 1.38 | 28 | 2319 | 1.46 | 28 | 2377 | 1.62 | 29 | 2492 | 1.94 | 31 | 2607 | 2.27 | 34 | 2720 | 2.62 | 35 | 2831 | 2.97 | 35
3380 | 1372 | 2442 | 1.67 | 31 | 2469 | 1.75 | 31 | 2523 | 1.92 | 32 | 2631 | 2.26 | 35 | 2739 | 2.62 | 37 | 2846 | 2.98 | 38
3595 | 1460 | 2594 | 2 | 33 | 2619 | 2.09 | 33 | 2670 | 2.26 | 35 | 2772 | 2.63 | 37 | 2873 | 3 | 40
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 1500CIEB
1500CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 15.00" • Outlet Dia. 22.19" • Outlet Area 2.68 ft² • Tip Speed FPM = 3.93 × RPM • Max BHP = 0.21 × (RPM÷1000)³ • FEG 56
Maximum RPM: Level 1 (A1) = 1940, Level 2 (A2) = 2587 ¦ Maximum Motor Frame: Level 1 (A1) = 184T, Level 2 (A2) = 215T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
1000 | 372 | 651 | 0.06 | 5.2 | 750 | 0.09 | 5.8 | 931 | 0.16 | 7.9 | 1250 | 0.34 | 12.5
1250 | 466 | 767 | 0.09 | 6.7 | 849 | 0.13 | 7.6 | 1003 | 0.21 | 9.1 | 1283 | 0.4 | 13.4 | 1533 | 0.64 | 17.2
1500 | 559 | 889 | 0.14 | 8.5 | 959 | 0.18 | 9.5 | 1093 | 0.27 | 10.5 | 1337 | 0.48 | 14.2 | 1567 | 0.73 | 17.8 | 1776 | 1 | 20
1750 | 652 | 1016 | 0.21 | 10.3 | 1076 | 0.25 | 11.6 | 1194 | 0.36 | 13 | 1413 | 0.58 | 16.1 | 1616 | 0.84 | 18.3 | 1812 | 1.13 | 21 | 1995 | 1.44 | 23 | 2166 | 1.79 | 24
2000 | 745 | 1144 | 0.29 | 12.6 | 1197 | 0.35 | 13.6 | 1302 | 0.46 | 15.6 | 1500 | 0.7 | 17.4 | 1685 | 0.97 | 19.7 | 1861 | 1.27 | 21 | 2033 | 1.6 | 24 | 2197 | 1.96 | 25 | 2352 | 2.34 | 26 | 2499 | 2.73 | 28
2250 | 838 | 1275 | 0.4 | 15 | 1322 | 0.46 | 15.9 | 1416 | 0.59 | 17.8 | 1596 | 0.85 | 19.1 | 1766 | 1.14 | 21 | 1927 | 1.45 | 23 | 2084 | 1.79 | 24 | 2238 | 2.16 | 25 | 2387 | 2.55 | 28 | 2529 | 2.96 | 30
2500 | 931 | 1406 | 0.53 | 17.7 | 1449 | 0.6 | 18.7 | 1534 | 0.74 | 19.8 | 1699 | 1.02 | 22 | 1856 | 1.33 | 22 | 2006 | 1.66 | 24 | 2150 | 2.01 | 25 | 2291 | 2.39 | 26 | 2431 | 2.79 | 28 | 2567 | 3.21 | 30
2750 | 1024 | 1539 | 0.7 | 19.8 | 1578 | 0.77 | 20 | 1655 | 0.92 | 22 | 1807 | 1.23 | 24 | 1953 | 1.56 | 24 | 2093 | 1.9 | 25 | 2228 | 2.27 | 27 | 2359 | 2.66 | 28 | 2487 | 3.07 | 29
3000 | 1117 | 1672 | 0.89 | 22 | 1707 | 0.97 | 23 | 1778 | 1.13 | 24 | 1918 | 1.46 | 26 | 2055 | 1.81 | 27 | 2186 | 2.18 | 26 | 2313 | 2.57 | 28 | 2437 | 2.97 | 30 | 2557 | 3.39 | 31
3250 | 1210 | 1805 | 1.12 | 24 | 1838 | 1.2 | 25 | 1904 | 1.37 | 26 | 2034 | 1.73 | 28 | 2161 | 2.1 | 29 | 2285 | 2.5 | 29 | 2404 | 2.9 | 29 | 2521 | 3.32 | 31
3500 | 1304 | 1939 | 1.38 | 26 | 1970 | 1.47 | 27 | 2031 | 1.65 | 28 | 2152 | 2.04 | 30 | 2271 | 2.43 | 32 | 2388 | 2.85 | 32 | 2501 | 3.27 | 31
3750 | 1397 | 2074 | 1.69 | 29 | 2102 | 1.78 | 29 | 2159 | 1.98 | 29 | 2272 | 2.38 | 32 | 2384 | 2.8 | 34 | 2494 | 3.23 | 35
4000 | 1490 | 2208 | 2.03 | 31 | 2235 | 2.13 | 31 | 2289 | 2.34 | 32 | 2395 | 2.77 | 34 | 2500 | 3.21 | 36
4250 | 1583 | 2343 | 2.42 | 32 | 2368 | 2.53 | 34 | 2419 | 2.75 | 34 | 2519 | 3.2 | 37
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 1650CIEB
1650CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 16.50" • Outlet Dia. 24.25" • Outlet Area 3.21 ft² • Tip Speed FPM = 4.32 × RPM • Max BHP = 0.34 × (RPM÷1000)³ • FEG 56
Maximum RPM: Level 1 (A1) = 1764, Level 2 (A2) = 2352 ¦ Maximum Motor Frame: Level 1 (A1) = 184T, Level 2 (A2) = 215T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
1200 | 374 | 588 | 0.07 | 5.3 | 679 | 0.1 | 5.9 | 844 | 0.19 | 8.2 | 1135 | 0.41 | 12.7
1515 | 472 | 698 | 0.11 | 7.1 | 773 | 0.16 | 7.9 | 913 | 0.25 | 9.5 | 1167 | 0.49 | 13.5 | 1394 | 0.77 | 17.8
1830 | 571 | 814 | 0.17 | 8.8 | 877 | 0.22 | 10 | 998 | 0.33 | 11 | 1219 | 0.59 | 15 | 1426 | 0.88 | 18.7 | 1616 | 1.22 | 22
2145 | 669 | 934 | 0.26 | 10.8 | 988 | 0.32 | 12.1 | 1094 | 0.44 | 13.6 | 1291 | 0.71 | 16.5 | 1474 | 1.02 | 19.9 | 1651 | 1.38 | 22 | 1817 | 1.76 | 24 | 1971 | 2.18 | 26
2460 | 767 | 1056 | 0.37 | 13.3 | 1103 | 0.44 | 14.2 | 1197 | 0.57 | 16.1 | 1375 | 0.87 | 18.1 | 1541 | 1.2 | 21 | 1699 | 1.57 | 23 | 1854 | 1.97 | 26 | 2002 | 2.4 | 27 | 2142 | 2.86 | 29 | 2275 | 3.34 | 30
2775 | 865 | 1179 | 0.51 | 15.9 | 1222 | 0.58 | 16.7 | 1305 | 0.74 | 18.9 | 1467 | 1.06 | 21 | 1619 | 1.42 | 22 | 1764 | 1.8 | 25 | 1904 | 2.21 | 26 | 2042 | 2.65 | 28 | 2176 | 3.13 | 30 | 2304 | 3.62 | 32
3090 | 964 | 1304 | 0.69 | 18.6 | 1342 | 0.77 | 19 | 1418 | 0.94 | 21 | 1565 | 1.29 | 24 | 1706 | 1.67 | 24 | 1840 | 2.07 | 26 | 1969 | 2.5 | 28 | 2095 | 2.95 | 29 | 2220 | 3.44 | 30 | 2342 | 3.96 | 32
3405 | 1062 | 1430 | 0.9 | 21 | 1464 | 0.99 | 22 | 1533 | 1.17 | 24 | 1668 | 1.55 | 26 | 1798 | 1.96 | 26 | 1924 | 2.39 | 27 | 2045 | 2.84 | 29 | 2162 | 3.31 | 31 | 2276 | 3.8 | 32
3720 | 1160 | 1556 | 1.16 | 24 | 1588 | 1.25 | 25 | 1651 | 1.45 | 26 | 1775 | 1.86 | 29 | 1896 | 2.29 | 29 | 2013 | 2.75 | 29 | 2127 | 3.22 | 31 | 2237 | 3.71 | 33 | 2345 | 4.23 | 33
4035 | 1258 | 1682 | 1.45 | 26 | 1712 | 1.56 | 27 | 1770 | 1.77 | 28 | 1885 | 2.21 | 31 | 1998 | 2.67 | 32 | 2108 | 3.16 | 32 | 2215 | 3.65 | 32 | 2319 | 4.17 | 33
4350 | 1356 | 1809 | 1.8 | 29 | 1837 | 1.92 | 30 | 1891 | 2.15 | 31 | 1998 | 2.62 | 33 | 2103 | 3.11 | 35 | 2207 | 3.62 | 36 | 2308 | 4.14 | 35
4665 | 1455 | 1937 | 2.21 | 32 | 1962 | 2.33 | 32 | 2012 | 2.57 | 33 | 2112 | 3.07 | 35 | 2211 | 3.59 | 37 | 2309 | 4.13 | 38
4980 | 1553 | 2064 | 2.67 | 34 | 2088 | 2.8 | 35 | 2135 | 3.05 | 35 | 2229 | 3.59 | 37 | 2322 | 4.14 | 39
5295 | 1651 | 2192 | 3.19 | 37 | 2214 | 3.33 | 37 | 2259 | 3.6 | 37 | 2347 | 4.16 | 39
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 1825CIEB
1825CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 18.25" • Outlet Dia. 30.38" • Outlet Area 5.03 ft² • Tip Speed FPM = 4.78 × RPM • Max BHP = 0.56 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 1589, Level 2 (A2) = 2118 ¦ Maximum Motor Frame: Level 1 (A1) = 184T, Level 2 (A2) = 215T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
1400 | 278 | 491 | 0.07 | 4.6 | 575 | 0.11 | 5.7 | 727 | 0.2 | 8.3
1800 | 358 | 592 | 0.11 | 6.5 | 653 | 0.16 | 7.6 | 783 | 0.26 | 9.2 | 1012 | 0.53 | 13.8
2200 | 437 | 697 | 0.17 | 8.5 | 749 | 0.23 | 9.7 | 853 | 0.35 | 10.7 | 1055 | 0.63 | 14.8 | 1239 | 0.97 | 19 | 1411 | 1.35 | 21
2600 | 517 | 805 | 0.26 | 10.6 | 851 | 0.33 | 11.9 | 936 | 0.46 | 13.3 | 1116 | 0.77 | 16.5 | 1280 | 1.12 | 19.4 | 1436 | 1.52 | 22 | 1584 | 1.95 | 24 | 1726 | 2.43 | 25
3000 | 596 | 915 | 0.38 | 12.9 | 956 | 0.45 | 13.8 | 1031 | 0.6 | 16.1 | 1186 | 0.93 | 18.6 | 1337 | 1.31 | 21 | 1477 | 1.72 | 22 | 1613 | 2.17 | 25 | 1744 | 2.66 | 26 | 1870 | 3.18 | 28 | 1992 | 3.74 | 31
3400 | 676 | 1027 | 0.53 | 15.6 | 1063 | 0.61 | 17 | 1132 | 0.78 | 18.8 | 1264 | 1.13 | 21 | 1404 | 1.54 | 22 | 1534 | 1.97 | 24 | 1657 | 2.43 | 25 | 1778 | 2.94 | 27 | 1896 | 3.48 | 28 | 2009 | 4.04 | 32
3800 | 755 | 1139 | 0.72 | 18.6 | 1172 | 0.81 | 19.8 | 1235 | 0.99 | 21 | 1352 | 1.37 | 24 | 1476 | 1.8 | 23 | 1600 | 2.27 | 25 | 1715 | 2.75 | 27 | 1825 | 3.26 | 28 | 1934 | 3.81 | 30 | 2041 | 4.4 | 33
4200 | 835 | 1252 | 0.95 | 21 | 1282 | 1.05 | 23 | 1341 | 1.25 | 24 | 1448 | 1.66 | 26 | 1555 | 2.1 | 26 | 1670 | 2.6 | 26 | 1780 | 3.12 | 28 | 1884 | 3.66 | 30 | 1985 | 4.22 | 32 | 2084 | 4.81 | 34
4600 | 914 | 1366 | 1.22 | 24 | 1394 | 1.33 | 25 | 1447 | 1.55 | 26 | 1548 | 2 | 28 | 1643 | 2.46 | 30 | 1745 | 2.97 | 28 | 1850 | 3.53 | 29 | 1950 | 4.1 | 32 | 2045 | 4.69 | 34
5000 | 994 | 1480 | 1.55 | 27 | 1506 | 1.67 | 27 | 1556 | 1.91 | 29 | 1650 | 2.4 | 32 | 1738 | 2.88 | 32 | 1828 | 3.41 | 32 | 1923 | 3.98 | 33 | 2020 | 4.59 | 34 | 2112 | 5.21 | 37
5400 | 1073 | 1595 | 1.93 | 30 | 1618 | 2.05 | 30 | 1665 | 2.32 | 31 | 1754 | 2.84 | 34 | 1837 | 3.37 | 36 | 1918 | 3.91 | 36 | 2003 | 4.49 | 36 | 2092 | 5.12 | 36
5800 | 1153 | 1709 | 2.36 | 32 | 1732 | 2.51 | 33 | 1775 | 2.78 | 34 | 1859 | 3.35 | 37 | 1938 | 3.91 | 39 | 2014 | 4.48 | 40 | 2090 | 5.08 | 41
6200 | 1232 | 1824 | 2.87 | 35 | 1845 | 3.02 | 36 | 1886 | 3.32 | 37 | 1965 | 3.92 | 39 | 2041 | 4.53 | 42 | 2112 | 5.12 | 45
6600 | 1312 | 1939 | 3.44 | 39 | 1959 | 3.6 | 39 | 1997 | 3.91 | 40 | 2072 | 4.55 | 43
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 2000CIEB
2000CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 20.00" • Outlet Dia. 33.47" • Outlet Area 6.11 ft² • Tip Speed FPM = 5.24 × RPM • Max BHP = 0.88 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 1449, Level 2 (A2) = 1932 ¦ Maximum Motor Frame: Level 1 (A1) = 184T, Level 2 (A2) = 215T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
2100 | 344 | 528 | 0.12 | 6.3 | 586 | 0.18 | 7.5 | 707 | 0.31 | 9.5 | 920 | 0.62 | 13.4
2550 | 417 | 617 | 0.19 | 8.3 | 666 | 0.26 | 9.5 | 766 | 0.4 | 10.7 | 953 | 0.73 | 14.4 | 1125 | 1.13 | 19.4 | 1286 | 1.59 | 22
3000 | 491 | 709 | 0.29 | 10.2 | 752 | 0.36 | 11.7 | 833 | 0.51 | 13.2 | 1003 | 0.88 | 16.2 | 1157 | 1.29 | 20 | 1303 | 1.77 | 23 | 1441 | 2.29 | 25
3450 | 565 | 803 | 0.41 | 12.5 | 842 | 0.49 | 13.5 | 913 | 0.66 | 15.5 | 1062 | 1.05 | 17.9 | 1202 | 1.49 | 22 | 1334 | 1.98 | 24 | 1462 | 2.52 | 26 | 1584 | 3.1 | 28 | 1702 | 3.72 | 30
3900 | 638 | 898 | 0.56 | 14.7 | 933 | 0.66 | 15.7 | 998 | 0.85 | 18.1 | 1125 | 1.26 | 20 | 1257 | 1.74 | 23 | 1378 | 2.24 | 25 | 1495 | 2.79 | 27 | 1609 | 3.39 | 29 | 1719 | 4.03 | 32 | 1826 | 4.71 | 33
4350 | 712 | 994 | 0.76 | 17.6 | 1025 | 0.86 | 18.3 | 1085 | 1.07 | 21 | 1197 | 1.51 | 24 | 1317 | 2.01 | 24 | 1432 | 2.56 | 26 | 1540 | 3.13 | 28 | 1645 | 3.74 | 30 | 1748 | 4.39 | 32 | 1848 | 5.08 | 34
4800 | 786 | 1090 | 0.99 | 21 | 1119 | 1.11 | 22 | 1174 | 1.34 | 23 | 1276 | 1.81 | 27 | 1381 | 2.33 | 26 | 1491 | 2.91 | 28 | 1593 | 3.51 | 30 | 1691 | 4.14 | 31 | 1786 | 4.81 | 33 | 1880 | 5.51 | 34
5250 | 859 | 1187 | 1.27 | 24 | 1214 | 1.4 | 24 | 1265 | 1.65 | 26 | 1360 | 2.16 | 29 | 1452 | 2.7 | 30 | 1552 | 3.3 | 29 | 1652 | 3.96 | 31 | 1744 | 4.61 | 33 | 1834 | 5.3 | 35 | 1921 | 6.01 | 35
5700 | 933 | 1285 | 1.6 | 26 | 1309 | 1.74 | 27 | 1357 | 2.02 | 28 | 1446 | 2.57 | 31 | 1531 | 3.14 | 33 | 1619 | 3.75 | 33 | 1712 | 4.43 | 32 | 1803 | 5.14 | 34 | 1888 | 5.85 | 35
6150 | 1007 | 1382 | 1.99 | 29 | 1405 | 2.14 | 30 | 1449 | 2.43 | 30 | 1534 | 3.03 | 34 | 1613 | 3.63 | 36 | 1692 | 4.26 | 36 | 1776 | 4.96 | 35 | 1863 | 5.7 | 36
6600 | 1080 | 1480 | 2.43 | 32 | 1501 | 2.59 | 32 | 1543 | 2.91 | 34 | 1623 | 3.55 | 36 | 1698 | 4.19 | 39 | 1771 | 4.85 | 39 | 1846 | 5.55 | 39 | 1926 | 6.32 | 38
7050 | 1154 | 1578 | 2.94 | 34 | 1598 | 3.11 | 35 | 1637 | 3.45 | 36 | 1713 | 4.14 | 39 | 1785 | 4.83 | 41 | 1853 | 5.51 | 42 | 1922 | 6.23 | 44
7500 | 1227 | 1676 | 3.52 | 37 | 1695 | 3.7 | 38 | 1732 | 4.06 | 39 | 1804 | 4.79 | 41 | 1873 | 5.52 | 44
7950 | 1301 | 1775 | 4.17 | 41 | 1793 | 4.36 | 41 | 1828 | 4.74 | 42 | 1896 | 5.51 | 44
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 2225CIEB
2225CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 22.25" • Outlet Dia. 36.50" • Outlet Area 7.27 ft² • Tip Speed FPM = 5.83 × RPM • Max BHP = 1.50 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 1303, Level 2 (A2) = 1737 ¦ Maximum Motor Frame: Level 1 (A1) = 215T, Level 2 (A2) = 256T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
2600 | 358 | 465 | 0.14 | 4.6 | 518 | 0.21 | 5.3 | 626 | 0.36 | 6.9 | 822 | 0.74 | 10.5
3200 | 440 | 550 | 0.23 | 6 | 593 | 0.3 | 6.9 | 681 | 0.48 | 7.8 | 848 | 0.88 | 11.3 | 1007 | 1.37 | 14.8
3800 | 523 | 638 | 0.35 | 7.5 | 675 | 0.44 | 8.4 | 747 | 0.62 | 9.9 | 895 | 1.07 | 12.6 | 1032 | 1.57 | 15.4 | 1166 | 2.15 | 18
4400 | 605 | 728 | 0.5 | 9.5 | 760 | 0.6 | 10.1 | 822 | 0.81 | 12 | 951 | 1.29 | 13.4 | 1075 | 1.83 | 16.4 | 1192 | 2.42 | 19 | 1308 | 3.08 | 21 | 1423 | 3.79 | 23
5000 | 688 | 819 | 0.7 | 11.6 | 847 | 0.82 | 12.3 | 903 | 1.06 | 14 | 1013 | 1.56 | 15.6 | 1128 | 2.15 | 17.8 | 1234 | 2.76 | 20 | 1338 | 3.44 | 22 | 1440 | 4.17 | 23 | 1541 | 4.95 | 26 | 1642 | 5.77 | 28
5600 | 771 | 911 | 0.96 | 13.9 | 936 | 1.08 | 14.6 | 986 | 1.35 | 15.7 | 1084 | 1.89 | 18.3 | 1186 | 2.51 | 18.7 | 1287 | 3.18 | 22 | 1381 | 3.88 | 23 | 1473 | 4.61 | 24 | 1565 | 5.42 | 26 | 1656 | 6.27 | 29
6200 | 853 | 1003 | 1.27 | 16 | 1026 | 1.41 | 16.8 | 1072 | 1.7 | 18.4 | 1160 | 2.29 | 21 | 1249 | 2.92 | 22 | 1343 | 3.64 | 23 | 1433 | 4.39 | 25 | 1518 | 5.16 | 26 | 1601 | 5.96 | 27 | 1685 | 6.83 | 30
6800 | 936 | 1096 | 1.64 | 18.9 | 1117 | 1.8 | 19.6 | 1159 | 2.11 | 21 | 1240 | 2.75 | 23 | 1320 | 3.42 | 25 | 1403 | 4.15 | 25 | 1489 | 4.96 | 26 | 1571 | 5.78 | 28 | 1648 | 6.61 | 29 | 1724 | 7.48 | 31
7400 | 1018 | 1189 | 2.08 | 22 | 1209 | 2.25 | 22 | 1247 | 2.59 | 23 | 1322 | 3.29 | 26 | 1396 | 4 | 28 | 1470 | 4.75 | 28 | 1548 | 5.58 | 27 | 1626 | 6.45 | 30 | 1701 | 7.35 | 31
8000 | 1101 | 1283 | 2.61 | 24 | 1301 | 2.79 | 25 | 1336 | 3.15 | 26 | 1406 | 3.9 | 29 | 1475 | 4.66 | 31 | 1542 | 5.44 | 32 | 1612 | 6.28 | 31 | 1685 | 7.2 | 32
8600 | 1183 | 1377 | 3.21 | 28 | 1393 | 3.4 | 28 | 1426 | 3.79 | 29 | 1492 | 4.59 | 32 | 1556 | 5.41 | 34 | 1619 | 6.23 | 35 | 1682 | 7.09 | 36
9200 | 1266 | 1470 | 3.9 | 30 | 1486 | 4.11 | 32 | 1517 | 4.52 | 32 | 1578 | 5.37 | 34 | 1639 | 6.24 | 37 | 1698 | 7.12 | 38
9800 | 1349 | 1564 | 4.68 | 34 | 1579 | 4.9 | 34 | 1608 | 5.34 | 36 | 1666 | 6.25 | 37 | 1723 | 7.17 | 40
10400 | 1431 | 1658 | 5.57 | 37 | 1672 | 5.8 | 37 | 1699 | 6.26 | 39
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 2450CIEB
2450CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 24.50" • Outlet Dia. 40.00" • Outlet Area 8.73 ft² • Tip Speed FPM = 6.41 × RPM • Max BHP = 2.43 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 1183, Level 2 (A2) = 1577 ¦ Maximum Motor Frame: Level 1 (A1) = 215T, Level 2 (A2) = 256T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
3200 | 367 | 427 | 0.18 | 4.7 | 474 | 0.26 | 5.6 | 571 | 0.45 | 7.2 | 748 | 0.91 | 11
3900 | 447 | 502 | 0.28 | 6.1 | 541 | 0.37 | 7.2 | 620 | 0.58 | 8.1 | 771 | 1.07 | 11.7 | 915 | 1.66 | 15.3
4600 | 527 | 579 | 0.42 | 7.7 | 612 | 0.53 | 8.5 | 678 | 0.75 | 10 | 813 | 1.29 | 12.8 | 937 | 1.9 | 16.1 | 1059 | 2.61 | 19.2
5300 | 607 | 657 | 0.6 | 9.6 | 687 | 0.72 | 10.1 | 744 | 0.98 | 12 | 861 | 1.55 | 13.9 | 974 | 2.2 | 17.2 | 1081 | 2.92 | 19.8 | 1187 | 3.72 | 22 | 1292 | 4.58 | 24
6000 | 688 | 737 | 0.83 | 11.5 | 763 | 0.97 | 12.2 | 814 | 1.25 | 13.7 | 915 | 1.86 | 15.9 | 1020 | 2.57 | 18.2 | 1117 | 3.31 | 21 | 1212 | 4.12 | 23 | 1306 | 5.02 | 25 | 1399 | 5.97 | 27 | 1491 | 6.94 | 29
6700 | 768 | 817 | 1.12 | 13.7 | 840 | 1.27 | 14.4 | 886 | 1.58 | 15.9 | 976 | 2.24 | 18.6 | 1070 | 2.98 | 19.6 | 1162 | 3.79 | 22 | 1249 | 4.63 | 25 | 1333 | 5.52 | 26 | 1418 | 6.5 | 28 | 1502 | 7.54 | 29
7400 | 848 | 898 | 1.47 | 16.1 | 919 | 1.64 | 16.8 | 961 | 1.99 | 17.8 | 1042 | 2.69 | 21 | 1125 | 3.46 | 22 | 1211 | 4.32 | 23 | 1293 | 5.21 | 26 | 1371 | 6.13 | 27 | 1448 | 7.11 | 29 | 1525 | 8.16 | 31
8100 | 928 | 979 | 1.9 | 18.9 | 998 | 2.08 | 19.1 | 1037 | 2.45 | 20 | 1112 | 3.22 | 23 | 1186 | 4.02 | 25 | 1263 | 4.91 | 25 | 1342 | 5.87 | 27 | 1416 | 6.84 | 28 | 1488 | 7.86 | 30 | 1558 | 8.9 | 32
8800 | 1008 | 1060 | 2.39 | 21 | 1078 | 2.59 | 22 | 1113 | 2.99 | 23 | 1183 | 3.82 | 26 | 1251 | 4.67 | 27 | 1320 | 5.58 | 28 | 1393 | 6.58 | 28 | 1465 | 7.63 | 30 | 1533 | 8.69 | 32
9500 | 1089 | 1142 | 2.98 | 24 | 1158 | 3.19 | 25 | 1191 | 3.62 | 26 | 1256 | 4.51 | 28 | 1319 | 5.41 | 31 | 1382 | 6.35 | 32 | 1448 | 7.38 | 31 | 1515 | 8.47 | 31
10200 | 1169 | 1224 | 3.66 | 27 | 1239 | 3.88 | 27 | 1270 | 4.35 | 28 | 1330 | 5.3 | 30 | 1390 | 6.26 | 33 | 1448 | 7.24 | 35 | 1507 | 8.28 | 35 | 1569 | 9.4 | 35
10900 | 1249 | 1305 | 4.42 | 30 | 1320 | 4.67 | 30 | 1349 | 5.16 | 32 | 1406 | 6.17 | 34 | 1462 | 7.2 | 36 | 1517 | 8.24 | 39 | 1571 | 9.3 | 39
11600 | 1329 | 1388 | 5.3 | 33 | 1401 | 5.55 | 33 | 1428 | 6.08 | 35 | 1482 | 7.15 | 38 | 1535 | 8.24 | 39
12300 | 1409 | 1470 | 6.28 | 36 | 1482 | 6.55 | 38 | 1508 | 7.11 | 38 | 1559 | 8.24 | 41
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 2700CIEB
2700CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 27.00" • Outlet Dia. 43.38" • Outlet Area 10.26 ft² • Tip Speed FPM = 7.07 × RPM • Max BHP = 4.25 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 1048, Level 2 (A2) = 1397 ¦ Maximum Motor Frame: Level 1 (A1) = 215T, Level 2 (A2) = 284T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
4000 | 390 | 404 | 0.26 | 5.6 | 441 | 0.36 | 6.6 | 519 | 0.59 | 7.5 | 666 | 1.14 | 10.4
4750 | 463 | 467 | 0.39 | 7.2 | 499 | 0.51 | 8.1 | 562 | 0.75 | 9.1 | 687 | 1.33 | 11.3
5500 | 536 | 531 | 0.56 | 8.8 | 559 | 0.69 | 9.6 | 613 | 0.97 | 11.1 | 726 | 1.6 | 12.6 | 828 | 2.3 | 15
6250 | 609 | 596 | 0.77 | 10.7 | 621 | 0.93 | 11.6 | 669 | 1.23 | 13.2 | 767 | 1.91 | 14.5 | 863 | 2.66 | 16.9 | 952 | 3.47 | 18.8
7000 | 682 | 662 | 1.05 | 13 | 684 | 1.21 | 13.3 | 727 | 1.55 | 14.8 | 813 | 2.28 | 16.8 | 903 | 3.09 | 18.6 | 985 | 3.95 | 21 | 1065 | 4.86 | 22 | 1153 | 5.94 | 24
7750 | 755 | 729 | 1.38 | 14.8 | 748 | 1.56 | 15.5 | 788 | 1.94 | 16.5 | 865 | 2.72 | 19.6 | 945 | 3.57 | 20 | 1025 | 4.5 | 23 | 1097 | 5.44 | 24 | 1169 | 6.45 | 25 | 1248 | 7.63 | 27
8500 | 828 | 795 | 1.78 | 17.5 | 814 | 1.98 | 17.5 | 850 | 2.39 | 19.4 | 920 | 3.23 | 23 | 991 | 4.13 | 24 | 1066 | 5.11 | 25 | 1137 | 6.13 | 26 | 1202 | 7.16 | 27 | 1268 | 8.27 | 28 | 1338 | 9.5 | 29
9250 | 901 | 862 | 2.25 | 19.5 | 879 | 2.47 | 21 | 912 | 2.91 | 22 | 978 | 3.83 | 25 | 1042 | 4.77 | 27 | 1109 | 5.79 | 27 | 1178 | 6.88 | 28 | 1242 | 7.99 | 30 | 1302 | 9.11 | 31 | 1362 | 10.3 | 31
10000 | 974 | 930 | 2.81 | 23 | 945 | 3.04 | 24 | 976 | 3.52 | 25 | 1037 | 4.5 | 28 | 1096 | 5.5 | 30 | 1157 | 6.57 | 31 | 1220 | 7.69 | 31 | 1283 | 8.87 | 32 | 1342 | 10.07 | 33
10750 | 1048 | 997 | 3.44 | 26 | 1012 | 3.7 | 27 | 1040 | 4.2 | 29 | 1097 | 5.25 | 32 | 1153 | 6.33 | 34 | 1208 | 7.42 | 35 | 1265 | 8.59 | 35 | 1325 | 9.84 | 35 | 1383 | 11.11 | 36
11500 | 1121 | 1065 | 4.18 | 29 | 1078 | 4.44 | 30 | 1105 | 4.99 | 32 | 1158 | 6.1 | 35 | 1211 | 7.25 | 37 | 1262 | 8.39 | 39 | 1315 | 9.62 | 39 | 1369 | 10.89 | 39
12250 | 1194 | 1133 | 5.02 | 33 | 1145 | 5.29 | 34 | 1171 | 5.88 | 35 | 1221 | 7.06 | 39 | 1270 | 8.26 | 41 | 1318 | 9.47 | 43 | 1367 | 10.74 | 43
13000 | 1267 | 1200 | 5.95 | 37 | 1212 | 6.25 | 37 | 1236 | 6.86 | 39 | 1283 | 8.1 | 41 | 1330 | 9.38 | 44 | 1376 | 10.67 | 46
13750 | 1340 | 1268 | 7 | 41 | 1280 | 7.33 | 41 | 1302 | 7.97 | 42 | 1347 | 9.29 | 45 | 1391 | 10.62 | 48
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 3000CIEB
3000CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 30.00" • Outlet Dia. 48.63" • Outlet Area 12.90 ft² • Tip Speed FPM = 7.85 × RPM • Max BHP = 7.19 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 943, Level 2 (A2) = 1257 ¦ Maximum Motor Frame: Level 1 (A1) = 215T, Level 2 (A2) = 284T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
4700 | 364 | 350 | 0.29 | 5.3 | 385 | 0.41 | 6.2 | 458 | 0.68 | 7.3
5600 | 434 | 404 | 0.43 | 6.8 | 434 | 0.57 | 7.9 | 494 | 0.87 | 8.8 | 610 | 1.56 | 11.2
6500 | 504 | 460 | 0.62 | 8.5 | 486 | 0.78 | 9.3 | 537 | 1.11 | 10.9 | 642 | 1.86 | 12.6 | 739 | 2.72 | 15.3
7400 | 574 | 516 | 0.86 | 10.3 | 539 | 1.03 | 10.9 | 584 | 1.4 | 13 | 678 | 2.23 | 14.3 | 764 | 3.11 | 16.7 | 851 | 4.14 | 19.2
8300 | 644 | 574 | 1.16 | 12.3 | 595 | 1.36 | 13.3 | 635 | 1.77 | 14.7 | 716 | 2.64 | 16 | 799 | 3.61 | 18.5 | 874 | 4.64 | 21 | 952 | 5.8 | 23
9200 | 713 | 632 | 1.53 | 14.1 | 651 | 1.75 | 14.8 | 687 | 2.19 | 16.5 | 759 | 3.13 | 18.9 | 835 | 4.16 | 19.8 | 908 | 5.28 | 22 | 975 | 6.42 | 24 | 1045 | 7.7 | 26
10100 | 783 | 690 | 1.97 | 16.5 | 707 | 2.21 | 17.3 | 741 | 2.7 | 18.3 | 807 | 3.71 | 21 | 874 | 4.8 | 22 | 944 | 5.99 | 24 | 1008 | 7.2 | 26 | 1068 | 8.45 | 27 | 1131 | 9.83 | 29 | 1200 | 11.41 | 30
11000 | 853 | 749 | 2.5 | 18.9 | 764 | 2.76 | 19.3 | 795 | 3.28 | 21 | 856 | 4.37 | 24 | 917 | 5.52 | 26 | 980 | 6.75 | 26 | 1043 | 8.05 | 28 | 1101 | 9.38 | 30 | 1157 | 10.76 | 30 | 1214 | 12.23 | 32
11900 | 923 | 808 | 3.13 | 21 | 822 | 3.4 | 22 | 851 | 3.97 | 23 | 907 | 5.13 | 27 | 963 | 6.34 | 29 | 1020 | 7.63 | 30 | 1079 | 8.99 | 31 | 1137 | 10.42 | 32 | 1190 | 11.85 | 33 | 1242 | 13.34 | 34
12800 | 993 | 867 | 3.84 | 24 | 880 | 4.14 | 25 | 907 | 4.75 | 27 | 960 | 6 | 30 | 1011 | 7.27 | 32 | 1063 | 8.6 | 33 | 1118 | 10.04 | 34 | 1173 | 11.53 | 34 | 1226 | 13.06 | 36
13700 | 1062 | 926 | 4.66 | 27 | 938 | 4.97 | 28 | 963 | 5.62 | 30 | 1013 | 6.96 | 33 | 1061 | 8.31 | 35 | 1110 | 9.72 | 37 | 1159 | 11.18 | 38 | 1210 | 12.72 | 38
14600 | 1132 | 985 | 5.59 | 31 | 997 | 5.94 | 31 | 1020 | 6.62 | 33 | 1067 | 8.04 | 36 | 1113 | 9.48 | 39 | 1158 | 10.94 | 41 | 1203 | 12.44 | 42 | 1250 | 14.04 | 42
15500 | 1202 | 1044 | 6.64 | 34 | 1055 | 7 | 35 | 1077 | 7.73 | 36 | 1121 | 9.21 | 40 | 1165 | 10.75 | 43 | 1208 | 12.3 | 45 | 1250 | 13.86 | 47
16400 | 1272 | 1104 | 7.84 | 38 | 1114 | 8.21 | 38 | 1135 | 8.98 | 41 | 1177 | 10.56 | 43 | 1218 | 12.15 | 47
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 3300CIEB
3300CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 33.00" • Outlet Dia. 52.00" • Outlet Area 14.75 ft² • Tip Speed FPM = 8.64 × RPM • Max BHP = 11.31 × (RPM÷1000)³ • FEG 60
Maximum RPM: Level 1 (A1) = 857, Level 2 (A2) = 1143 ¦ Maximum Motor Frame: Level 1 (A1) = 215T, Level 2 (A2) = 286T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
5800 | 393 | 325 | 0.36 | 4.9 | 358 | 0.51 | 5.8 | 421 | 0.84 | 7.1
6900 | 468 | 375 | 0.54 | 6.6 | 402 | 0.7 | 7.6 | 457 | 1.08 | 8.3 | 564 | 1.96 | 11.5
8000 | 542 | 426 | 0.77 | 8.7 | 450 | 0.96 | 9.6 | 498 | 1.38 | 10.4 | 590 | 2.31 | 12.4 | 683 | 3.39 | 15.3
9100 | 617 | 478 | 1.07 | 10.4 | 500 | 1.29 | 11.1 | 542 | 1.74 | 12.5 | 624 | 2.75 | 13.9 | 705 | 3.9 | 16.8 | 787 | 5.15 | 19.4
10200 | 692 | 531 | 1.45 | 12.5 | 550 | 1.69 | 13.2 | 588 | 2.18 | 14.8 | 662 | 3.27 | 15.6 | 734 | 4.46 | 18.4 | 806 | 5.79 | 21 | 880 | 7.2 | 22
11300 | 766 | 585 | 1.92 | 14.4 | 602 | 2.18 | 14.7 | 636 | 2.71 | 16.5 | 704 | 3.9 | 18.5 | 769 | 5.15 | 20 | 834 | 6.52 | 22 | 899 | 8.01 | 24 | 966 | 9.59 | 25
12400 | 841 | 639 | 2.49 | 16.5 | 654 | 2.76 | 17 | 685 | 3.34 | 18.4 | 747 | 4.59 | 22 | 808 | 5.95 | 22 | 867 | 7.37 | 24 | 926 | 8.9 | 26 | 986 | 10.57 | 26 | 1046 | 12.28 | 28 | 1109 | 14.03 | 31
13500 | 915 | 693 | 3.16 | 19.2 | 707 | 3.45 | 19.4 | 735 | 4.06 | 21 | 792 | 5.4 | 24 | 849 | 6.85 | 25 | 904 | 8.36 | 25 | 958 | 9.93 | 27 | 1012 | 11.61 | 29 | 1067 | 13.43 | 30 | 1122 | 15.28 | 32
14600 | 990 | 747 | 3.94 | 22 | 760 | 4.25 | 22 | 786 | 4.91 | 24 | 839 | 6.33 | 27 | 892 | 7.87 | 28 | 943 | 9.45 | 29 | 993 | 11.08 | 29 | 1044 | 12.84 | 31 | 1094 | 14.67 | 33
15700 | 1064 | 801 | 4.84 | 25 | 813 | 5.17 | 25 | 838 | 5.89 | 27 | 887 | 7.38 | 30 | 936 | 8.99 | 31 | 985 | 10.69 | 33 | 1032 | 12.41 | 32 | 1078 | 14.18 | 33 | 1125 | 16.07 | 35
16800 | 1139 | 856 | 5.89 | 28 | 867 | 6.24 | 28 | 890 | 6.99 | 30 | 936 | 8.57 | 32 | 982 | 10.26 | 34 | 1027 | 12.01 | 35 | 1072 | 13.85 | 36 | 1116 | 15.72 | 36
17900 | 1214 | 910 | 7.05 | 30 | 921 | 7.45 | 31 | 942 | 8.23 | 32 | 985 | 9.88 | 34 | 1028 | 11.64 | 37 | 1071 | 13.49 | 39 | 1114 | 15.43 | 39
19000 | 1288 | 965 | 8.39 | 34 | 975 | 8.8 | 34 | 995 | 9.63 | 34 | 1036 | 11.39 | 37 | 1076 | 13.2 | 40 | 1117 | 15.15 | 42
20100 | 1363 | 1020 | 9.89 | 37 | 1029 | 10.31 | 37 | 1048 | 11.19 | 39 | 1087 | 13.04 | 40 | 1125 | 14.94 | 43
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 3650CIEB
3650CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 36.50" • Outlet Dia. 54.63" • Outlet Area 16.27 ft² • Tip Speed FPM = 9.56 × RPM • Max BHP = 18.48 × (RPM÷1000)³ • FEG 56
Maximum RPM: Level 1 (A1) = 746, Level 2 (A2) = 995 ¦ Maximum Motor Frame: Level 1 (A1) = 256T, Level 2 (A2) = 286T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
7100 | 436 | 296 | 0.45 | 5 | 326 | 0.63 | 5.7 | 387 | 1.06 | 6.6
8400 | 516 | 339 | 0.66 | 6.6 | 365 | 0.87 | 7.4 | 417 | 1.34 | 8.1 | 513 | 2.4 | 10
9700 | 596 | 384 | 0.93 | 8.6 | 407 | 1.17 | 9.7 | 451 | 1.69 | 10.4 | 539 | 2.85 | 11.4
10000 | 614 | 395 | 1.01 | 9 | 417 | 1.26 | 10.2 | 460 | 1.78 | 11 | 546 | 2.97 | 11.7
12300 | 756 | 476 | 1.73 | 12.6 | 494 | 2.02 | 13.4 | 530 | 2.64 | 14.6 | 600 | 3.99 | 15 | 670 | 5.49 | 16.5 | 732 | 7.04 | 18.5
13600 | 836 | 523 | 2.27 | 14.6 | 539 | 2.58 | 15.2 | 572 | 3.26 | 16.4 | 635 | 4.71 | 17.7 | 699 | 6.29 | 18.5 | 759 | 7.96 | 21 | 816 | 9.72 | 23
14900 | 916 | 570 | 2.91 | 16.4 | 585 | 3.26 | 17.2 | 615 | 3.99 | 18.8 | 672 | 5.52 | 21 | 731 | 7.22 | 21 | 789 | 9.01 | 23 | 842 | 10.85 | 25 | 894 | 12.79 | 26
16200 | 995 | 617 | 3.67 | 18.8 | 631 | 4.05 | 18.9 | 658 | 4.82 | 21 | 712 | 6.48 | 24 | 765 | 8.25 | 25 | 819 | 10.13 | 26 | 872 | 12.13 | 28 | 920 | 14.14 | 28 | 967 | 16.21 | 30
17500 | 1075 | 664 | 4.55 | 21 | 677 | 4.96 | 22 | 703 | 5.81 | 24 | 753 | 7.57 | 27 | 801 | 9.4 | 29 | 851 | 11.38 | 30 | 902 | 13.51 | 31 | 949 | 15.62 | 32 | 993 | 17.79 | 33
18800 | 1155 | 712 | 5.59 | 24 | 724 | 6.02 | 25 | 748 | 6.92 | 27 | 794 | 8.76 | 31 | 840 | 10.73 | 33 | 886 | 12.81 | 34 | 933 | 15 | 33 | 979 | 17.25 | 35
20100 | 1235 | 760 | 6.77 | 28 | 771 | 7.23 | 28 | 793 | 8.17 | 30 | 837 | 10.15 | 34 | 880 | 12.21 | 37 | 922 | 14.34 | 38 | 966 | 16.64 | 38
21400 | 1315 | 807 | 8.09 | 31 | 818 | 8.59 | 33 | 839 | 9.6 | 34 | 880 | 11.67 | 38 | 921 | 13.85 | 40 | 961 | 16.11 | 42
22700 | 1395 | 855 | 9.59 | 35 | 865 | 10.12 | 36 | 885 | 11.19 | 38 | 924 | 13.37 | 41 | 962 | 15.62 | 45
24000 | 1475 | 903 | 11.28 | 40 | 912 | 11.81 | 40 | 931 | 12.94 | 41 | 968 | 15.24 | 44
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 4025CIEB
4025CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 40.25" • Outlet Dia. 60.63" • Outlet Area 20.05 ft² • Tip Speed FPM = 10.54 × RPM • Max BHP = 30.12 × (RPM÷1000)³ • FEG 56
Maximum RPM: Level 1 (A1) = 677, Level 2 (A2) = 903 ¦ Maximum Motor Frame: Level 1 (A1) = 256T, Level 2 (A2) = 286T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
9800 | 489 | 297 | 0.72 | 6.1 | 322 | 0.98 | 6.9 | 371 | 1.54 | 7.5
11200 | 559 | 333 | 1 | 7.7 | 355 | 1.28 | 8.6 | 397 | 1.88 | 9.4 | 479 | 3.25 | 11.4
12600 | 629 | 370 | 1.35 | 9.4 | 389 | 1.65 | 10.5 | 426 | 2.3 | 12.1 | 502 | 3.78 | 12.8 | 571 | 5.4 | 14.4
14000 | 698 | 406 | 1.76 | 11.8 | 424 | 2.1 | 12.7 | 458 | 2.81 | 14.2 | 527 | 4.4 | 13.9 | 591 | 6.12 | 16
15400 | 768 | 444 | 2.28 | 14.1 | 460 | 2.64 | 14.5 | 491 | 3.41 | 16.1 | 553 | 5.09 | 16.3 | 615 | 6.94 | 17.2 | 670 | 8.86 | 19
16800 | 838 | 481 | 2.87 | 14.4 | 496 | 3.27 | 16.1 | 525 | 4.1 | 17.5 | 581 | 5.87 | 18.7 | 639 | 7.84 | 19 | 693 | 9.9 | 21 | 743 | 12.02 | 23
18200 | 908 | 519 | 3.58 | 17.2 | 533 | 4.02 | 18 | 559 | 4.89 | 19.3 | 611 | 6.76 | 21 | 664 | 8.82 | 21 | 717 | 11.03 | 23 | 765 | 13.28 | 25 | 811 | 15.59 | 26
19600 | 978 | 557 | 4.4 | 19.3 | 570 | 4.87 | 19.6 | 595 | 5.82 | 21 | 643 | 7.79 | 23 | 691 | 9.92 | 24 | 741 | 12.23 | 25 | 789 | 14.65 | 27 | 832 | 17.05 | 29 | 876 | 19.63 | 31
21000 | 1048 | 595 | 5.34 | 21 | 607 | 5.84 | 21 | 630 | 6.83 | 22 | 676 | 8.95 | 26 | 721 | 11.19 | 27 | 767 | 13.59 | 28 | 813 | 16.11 | 30 | 856 | 18.68 | 32 | 896 | 21.27 | 33
22400 | 1117 | 633 | 6.41 | 23 | 644 | 6.93 | 24 | 666 | 7.99 | 25 | 709 | 10.21 | 29 | 751 | 12.54 | 32 | 794 | 15.05 | 32 | 837 | 17.65 | 32 | 880 | 20.39 | 34
23800 | 1187 | 671 | 7.61 | 26 | 682 | 8.18 | 26 | 702 | 9.28 | 28 | 743 | 11.63 | 32 | 783 | 14.09 | 35 | 823 | 16.68 | 36 | 863 | 19.36 | 36
25200 | 1257 | 710 | 8.99 | 29 | 719 | 9.54 | 29 | 739 | 10.74 | 32 | 778 | 13.22 | 36 | 816 | 15.8 | 38 | 853 | 18.45 | 40 | 891 | 21.26 | 41
26600 | 1327 | 748 | 10.49 | 32 | 757 | 11.09 | 34 | 776 | 12.35 | 36 | 813 | 14.94 | 38 | 849 | 17.63 | 42 | 884 | 20.38 | 45
28000 | 1397 | 786 | 12.15 | 36 | 795 | 12.8 | 36 | 813 | 14.12 | 38 | 848 | 16.82 | 43 | 882 | 19.59 | 46
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 4450CIEB
4450CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 44.50" • Outlet Dia. 66.75" • Outlet Area 24.30 ft² • Tip Speed FPM = 11.65 × RPM • Max BHP = 49.74 × (RPM÷1000)³ • FEG 56
Maximum RPM: Level 1 (A1) = 613, Level 2 (A2) = 817 ¦ Maximum Motor Frame: Level 1 (A1) = 284T, Level 2 (A2) = 324T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
12000 | 494 | 269 | 0.89 | 6.2 | 291 | 1.19 | 7.1 | 335 | 1.87 | 7.5
13900 | 572 | 305 | 1.27 | 7.8 | 325 | 1.62 | 8.8 | 362 | 2.35 | 9.7 | 435 | 4.03 | 12.2
15800 | 650 | 342 | 1.75 | 9.7 | 359 | 2.14 | 10.8 | 392 | 2.95 | 12.4 | 459 | 4.78 | 13.8 | 520 | 6.79 | 15.3
17700 | 728 | 379 | 2.35 | 12.2 | 395 | 2.79 | 13.6 | 424 | 3.66 | 15.3 | 484 | 5.64 | 15.3 | 542 | 7.82 | 17.1 | 595 | 10.08 | 18.4
19600 | 807 | 417 | 3.1 | 15 | 431 | 3.57 | 16 | 458 | 4.54 | 17.2 | 511 | 6.62 | 18.7 | 566 | 8.97 | 18.7 | 615 | 11.38 | 20 | 664 | 13.96 | 21
21500 | 885 | 455 | 4 | 17.1 | 467 | 4.49 | 18 | 492 | 5.53 | 19.3 | 541 | 7.79 | 21 | 591 | 10.27 | 20 | 639 | 12.86 | 22 | 683 | 15.55 | 24 | 728 | 18.41 | 25
23400 | 963 | 493 | 5.05 | 19.3 | 504 | 5.58 | 19.8 | 527 | 6.7 | 21 | 572 | 9.09 | 23 | 617 | 11.68 | 23 | 663 | 14.45 | 24 | 706 | 17.31 | 26 | 746 | 20.24 | 28 | 787 | 23.33 | 30
25300 | 1041 | 531 | 6.28 | 22 | 542 | 6.88 | 22 | 563 | 8.07 | 23 | 605 | 10.62 | 25 | 646 | 13.32 | 26 | 688 | 16.2 | 26 | 731 | 19.33 | 29 | 770 | 22.43 | 30 | 806 | 25.53 | 33
27200 | 1119 | 569 | 7.69 | 23 | 579 | 8.32 | 24 | 599 | 9.61 | 25 | 638 | 12.3 | 29 | 677 | 15.19 | 30 | 715 | 18.16 | 31 | 755 | 21.39 | 32 | 794 | 24.73 | 34
29100 | 1197 | 607 | 9.31 | 25 | 617 | 10.01 | 27 | 636 | 11.4 | 29 | 672 | 14.21 | 31 | 708 | 17.2 | 34 | 744 | 20.36 | 35 | 781 | 23.7 | 36
31000 | 1276 | 646 | 11.18 | 29 | 655 | 11.91 | 29 | 672 | 13.33 | 31 | 707 | 16.37 | 35 | 741 | 19.52 | 39 | 775 | 22.84 | 40 | 808 | 26.18 | 42
32900 | 1354 | 684 | 13.24 | 32 | 693 | 14.04 | 33 | 709 | 15.54 | 35 | 742 | 18.73 | 39 | 774 | 22.02 | 43 | 806 | 25.47 | 45
34800 | 1432 | 723 | 15.61 | 37 | 731 | 16.41 | 37 | 747 | 18.06 | 39 | 778 | 21.39 | 44 | 808 | 24.8 | 46
36700 | 1510 | 761 | 18.17 | 41 | 769 | 19.04 | 42 | 784 | 20.75 | 44 | 814 | 24.3 | 47
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.

## 4900CIEB
4900CIEB — Tubular Centrifugal Inline Fan
Wheel Dia. 49.00" • Outlet Dia. 72.75" • Outlet Area 28.87 ft² • Tip Speed FPM = 12.83 × RPM • Max BHP = 80.56 × (RPM÷1000)³ • FEG 56
Maximum RPM: Level 1 (A1) = 557, Level 2 (A2) = 742 ¦ Maximum Motor Frame: Level 1 (A1) = 284T, Level 2 (A2) = 326T
CFM | OV | STATIC PRESSURE (IN. W.G.)
|  | 0.125 |  |  | 0.25 |  |  | 0.50 |  |  | 1.00 |  |  | 1.50 |  |  | 2.00 |  |  | 2.50 |  |  | 3.00 |  |  | 3.50 |  |  | 4.00
|  | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones | RPM | BHP | Sones
14400 | 499 | 242 | 1.05 | 6.3 | 263 | 1.43 | 7 | 303 | 2.24 | 7.5
16500 | 572 | 272 | 1.46 | 7.8 | 290 | 1.87 | 8.6 | 325 | 2.76 | 9.2 | 392 | 4.76 | 11.8
18600 | 644 | 302 | 1.96 | 9.3 | 318 | 2.42 | 10.6 | 349 | 3.38 | 11.9 | 412 | 5.58 | 13.4 | 468 | 7.94 | 15.7
20700 | 717 | 333 | 2.59 | 11.2 | 348 | 3.11 | 12.4 | 376 | 4.16 | 14.3 | 432 | 6.48 | 15.5 | 485 | 9.04 | 17
22800 | 790 | 364 | 3.35 | 13.9 | 377 | 3.89 | 14.8 | 403 | 5.04 | 16.5 | 454 | 7.53 | 17.5 | 505 | 10.28 | 18.6 | 550 | 13.1 | 20
24900 | 863 | 395 | 4.25 | 16.3 | 407 | 4.84 | 17.2 | 431 | 6.07 | 19.1 | 477 | 8.69 | 20 | 525 | 11.63 | 19.9 | 569 | 14.65 | 22 | 610 | 17.78 | 23
27000 | 935 | 427 | 5.33 | 18.9 | 438 | 5.96 | 19.3 | 460 | 7.28 | 21 | 503 | 10.08 | 22 | 546 | 13.11 | 22 | 589 | 16.34 | 23 | 629 | 19.73 | 25 | 667 | 23.19 | 27
29100 | 1008 | 458 | 6.55 | 21 | 469 | 7.25 | 22 | 489 | 8.63 | 23 | 529 | 11.6 | 25 | 569 | 14.8 | 25 | 609 | 18.16 | 25 | 649 | 21.8 | 27 | 684 | 25.34 | 28 | 720 | 29.15 | 30
31200 | 1081 | 490 | 7.98 | 23 | 500 | 8.72 | 23 | 519 | 10.21 | 25 | 556 | 13.31 | 27 | 593 | 16.65 | 27 | 631 | 20.24 | 27 | 668 | 23.9 | 29 | 704 | 27.78 | 30 | 737 | 31.67 | 33
33300 | 1154 | 522 | 9.61 | 25 | 531 | 10.38 | 26 | 549 | 11.96 | 27 | 584 | 15.25 | 30 | 618 | 18.68 | 30 | 653 | 22.39 | 31 | 689 | 26.32 | 31 | 724 | 30.37 | 33
35400 | 1226 | 553 | 11.39 | 27 | 562 | 12.24 | 28 | 579 | 13.91 | 29 | 612 | 17.36 | 32 | 645 | 21.04 | 33 | 677 | 24.82 | 35 | 710 | 28.83 | 35
37500 | 1299 | 585 | 13.45 | 30 | 593 | 14.31 | 30 | 609 | 16.07 | 31 | 641 | 19.75 | 34 | 672 | 23.57 | 37 | 702 | 27.48 | 38 | 733 | 31.65 | 40
39600 | 1372 | 617 | 15.74 | 32 | 625 | 16.68 | 32 | 640 | 18.52 | 34 | 670 | 22.35 | 37 | 700 | 26.4 | 41 | 728 | 30.41 | 43
41700 | 1445 | 649 | 18.28 | 35 | 656 | 19.22 | 35 | 671 | 21.21 | 38 | 699 | 25.16 | 41 | 728 | 29.42 | 45
Note: Performance certified for Installation Type B: free inlet, ducted outlet, at standard air density. OV = outlet velocity (FPM). Under each static pressure: RPM = fan speed, BHP = brake horsepower (excludes drive/transmission losses), Sones = loudness at 5 ft (1.5 m), hemispherical free field per AMCA Standard 301. Ratings exclude the effect of accessories.
Note: Ratings read left to right from 0.125" SP. RPM above the Level 1 (A1) maximum require Level 2 (A2) construction; selections above the Level 2 maximum are not available. These ratings apply to both TCLB and TCLBR (restaurant) models.