## 1650HPB
1650HPB — Backward Curved High Pressure Fan
Outlet Area: 1.57 ft² Wheel Diameter: 16.50" Tip Speed (FPM): 4.32 x RPM
Max. RPM — Design 14: 3241 Design 17: 4399 Design 22: NA Design 26: NA
CFM | OV (FPM) | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 2.5" SP |  | 3" SP |  | 3.5" SP |  | 4" SP |  | 4.5" SP |  | 5" SP |  | 5.5" SP |  | 6" SP |  | 6.5" SP |  | 7" SP |  | 7.5" SP |  | 8" SP |  | 8.5" SP |  | 9" SP |  | 9.5" SP |  | 10" SP |  | 10.5" SP |  | 11" SP |  | 11.5" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1000 | 637 | 774 | 0.12 | 1031 | 0.26
1200 | 764 | 827 | 0.14 | 1051 | 0.28
1400 | 892 | 885 | 0.17 | 1091 | 0.32 | 1276 | 0.5 | 1457 | 0.72
1600 | 1019 | 947 | 0.21 | 1141 | 0.37 | 1311 | 0.55 | 1471 | 0.76 | 1630 | 1.02
1800 | 1146 | 1017 | 0.25 | 1199 | 0.43 | 1355 | 0.62 | 1503 | 0.83 | 1646 | 1.07 | 1787 | 1.34
2000 | 1274 | 1094 | 0.31 | 1258 | 0.5 | 1409 | 0.71 | 1546 | 0.92 | 1678 | 1.16 | 1806 | 1.41 | 1933 | 1.71 | 2060 | 2.05
2200 | 1401 | 1173 | 0.38 | 1319 | 0.57 | 1466 | 0.79 | 1596 | 1.02 | 1720 | 1.27 | 1840 | 1.53 | 1956 | 1.8 | 2071 | 2.11 | 2187 | 2.47
2400 | 1529 | 1254 | 0.45 | 1386 | 0.65 | 1525 | 0.89 | 1652 | 1.14 | 1768 | 1.39 | 1881 | 1.66 | 1991 | 1.94 | 2098 | 2.24 | 2204 | 2.56
2600 | 1656 | 1336 | 0.54 | 1459 | 0.75 | 1585 | 0.99 | 1710 | 1.26 | 1823 | 1.53 | 1929 | 1.8 | 2033 | 2.09 | 2135 | 2.4 | 2234 | 2.71 | 2332 | 3.05 | 2429 | 3.42 | 2528 | 3.83 | 2625 | 4.26 | 2721 | 4.71
2800 | 1783 | 1418 | 0.63 | 1535 | 0.86 | 1649 | 1.11 | 1769 | 1.39 | 1880 | 1.68 | 1983 | 1.97 | 2081 | 2.26 | 2178 | 2.58 | 2272 | 2.9 | 2365 | 3.24 | 2456 | 3.59 | 2547 | 3.97 | 2637 | 4.37 | 2729 | 4.81 | 2819 | 5.28 | 2908 | 5.76
3000 | 1911 | 1502 | 0.74 | 1613 | 0.99 | 1718 | 1.24 | 1829 | 1.53 | 1939 | 1.84 | 2040 | 2.14 | 2134 | 2.45 | 2226 | 2.77 | 2316 | 3.11 | 2405 | 3.45 | 2492 | 3.8 | 2578 | 4.17 | 2662 | 4.56 | 2747 | 4.97 | 2831 | 5.41 | 2916 | 5.88 | 3001 | 6.38 | 3084 | 6.89
3200 | 2038 | 1587 | 0.86 | 1694 | 1.13 | 1792 | 1.39 | 1893 | 1.68 | 1998 | 2 | 2098 | 2.33 | 2191 | 2.66 | 2279 | 2.99 | 2365 | 3.33 | 2450 | 3.68 | 2533 | 4.04 | 2615 | 4.42 | 2696 | 4.8 | 2776 | 5.2 | 2855 | 5.62 | 2934 | 6.06 | 3013 | 6.52 | 3093 | 7.03
3400 | 2166 | 1672 | 1 | 1775 | 1.28 | 1868 | 1.55 | 1961 | 1.85 | 2059 | 2.18 | 2157 | 2.52 | 2249 | 2.87 | 2335 | 3.22 | 2418 | 3.57 | 2499 | 3.93 | 2579 | 4.3 | 2658 | 4.69 | 2736 | 5.08 | 2812 | 5.48 | 2888 | 5.89 | 2963 | 6.32 | 3037 | 6.76 | 3112 | 7.23
3600 | 2293 | 1758 | 1.15 | 1857 | 1.45 | 1946 | 1.74 | 2033 | 2.04 | 2123 | 2.37 | 2216 | 2.72 | 2307 | 3.09 | 2393 | 3.46 | 2474 | 3.83 | 2553 | 4.2 | 2629 | 4.58 | 2705 | 4.97 | 2780 | 5.38 | 2854 | 5.79 | 2926 | 6.2 | 2998 | 6.63 | 3070 | 7.07 | 3140 | 7.52 | 3211 | 8 | 3281 | 8.49 | 3351 | 9.01 | 3421 | 9.55 | 3492 | 10.12 | 3562 | 10.7 | 3702 | 11.94
3800 | 2420 | 1844 | 1.31 | 1939 | 1.63 | 2026 | 1.94 | 2108 | 2.25 | 2191 | 2.58 | 2278 | 2.94 | 2366 | 3.32 | 2452 | 3.72 | 2532 | 4.1 | 2609 | 4.49 | 2683 | 4.88 | 2756 | 5.28 | 2827 | 5.69 | 2899 | 6.11 | 2969 | 6.54 | 3039 | 6.98 | 3107 | 7.42 | 3175 | 7.87 | 3243 | 8.34 | 3310 | 8.82 | 3376 | 9.31 | 3442 | 9.82 | 3509 | 10.37 | 3575 | 10.92 | 3709 | 12.12 | 3842 | 13.4 | 3972 | 14.72
4000 | 2548 | 1931 | 1.49 | 2022 | 1.83 | 2106 | 2.16 | 2185 | 2.48 | 2263 | 2.82 | 2344 | 3.18 | 2427 | 3.57 | 2511 | 3.98 | 2591 | 4.39 | 2667 | 4.8 | 2740 | 5.21 | 2810 | 5.61 | 2880 | 6.03 | 2948 | 6.46 | 3015 | 6.89 | 3083 | 7.34 | 3149 | 7.79 | 3215 | 8.26 | 3280 | 8.72 | 3344 | 9.2 | 3408 | 9.69 | 3472 | 10.2 | 3535 | 10.71 | 3598 | 11.25 | 3724 | 12.38 | 3851 | 13.61 | 3977 | 14.91
4200 | 2675 | [18 empty] | 2725 | 5.11 | 2798 | 5.54 | 2867 | 5.97 | 2935 | 6.4 | 3001 | 6.83 | 3066 | 7.27 | 3130 | 7.72 | 3195 | 8.19 | 3258 | 8.66 | 3321 | 9.14 | 3384 | 9.63 | 3446 | 10.12 | 3507 | 10.62 | 3568 | 11.13 | 3628 | 11.65 | 3748 | 12.75 | 3868 | 13.91 | 3988 | 15.16
4400 | 2803 | [18 empty] | 2784 | 5.43 | 2856 | 5.88 | 2925 | 6.33 | 2992 | 6.78 | 3056 | 7.23 | 3120 | 7.69 | 3182 | 8.14 | 3244 | 8.61 | 3305 | 9.09 | 3366 | 9.58 | 3427 | 10.08 | 3487 | 10.58 | 3546 | 11.08 | 3605 | 11.6 | 3664 | 12.13 | 3779 | 13.2 | 3894 | 14.33
4600 | 2930 | [18 empty] | 2843 | 5.76 | 2915 | 6.24 | 2984 | 6.71 | 3050 | 7.18 | 3113 | 7.64 | 3175 | 8.11 | 3236 | 8.58 | 3296 | 9.06 | 3355 | 9.54 | 3414 | 10.04 | 3473 | 10.55 | 3531 | 11.06 | 3589 | 11.58 | 3646 | 12.1 | 3703 | 12.63 | 3815 | 13.71 | 3926 | 14.83
4800 | 3057 | [18 empty] | 2904 | 6.12 | 2974 | 6.6 | 3042 | 7.09 | 3108 | 7.59 | 3172 | 8.08 | 3233 | 8.56 | 3293 | 9.05 | 3351 | 9.54 | 3409 | 10.04 | 3466 | 10.54 | 3522 | 11.04 | 3579 | 11.57 | 3635 | 12.09 | 3690 | 12.62 | 3746 | 13.17 | 3855 | 14.27 | 3962 | 15.39
5000 | 3185 | [18 empty] | 2968 | 6.5 | 3035 | 6.99 | 3101 | 7.49 | 3166 | 8 | 3230 | 8.52 | 3291 | 9.03 | 3350 | 9.53 | 3408 | 10.04 | 3465 | 10.55 | 3520 | 11.06 | 3575 | 11.58 | 3630 | 12.11 | 3684 | 12.64 | 3737 | 13.17 | 3791 | 13.72 | 3898 | 14.85
5200 | 3312 | [18 empty] | 3034 | 6.9 | 3097 | 7.39 | 3162 | 7.91 | 3225 | 8.43 | 3288 | 8.96 | 3349 | 9.5 | 3409 | 10.03 | 3466 | 10.56 | 3522 | 11.09 | 3576 | 11.61 | 3630 | 12.14 | 3683 | 12.67 | 3736 | 13.22 | 3788 | 13.76 | 3840 | 14.32 | 3943 | 15.45
5400 | 3439 | [18 empty] | 3103 | 7.33 | 3163 | 7.83 | 3224 | 8.35 | 3286 | 8.89 | 3347 | 9.43 | 3408 | 9.98 | 3467 | 10.54 | 3524 | 11.09 | 3580 | 11.64 | 3634 | 12.18 | 3687 | 12.73 | 3739 | 13.27 | 3790 | 13.82 | 3841 | 14.38 | 3891 | 14.94 | 3991 | 16.08
5600 | 3567 | [18 empty] | 3174 | 7.8 | 3231 | 8.3 | 3289 | 8.82 | 3348 | 9.36 | 3408 | 9.92 | 3467 | 10.48 | 3525 | 11.05 | 3582 | 11.62 | 3638 | 12.2 | 3692 | 12.77 | 3744 | 13.33 | 3796 | 13.9 | 3846 | 14.46 | 3896 | 15.03 | 3945 | 15.59
5800 | 3694 | [36 empty] | 3750 | 13.36 | 3802 | 13.94 | 3854 | 14.54 | 3904 | 15.12 | 3953 | 15.7
6000 | 3822 | [36 empty] | 3808 | 13.96 | 3861 | 14.58 | 3912 | 15.19 | 3961 | 15.79
6200 | 3949 | [36 empty] | 3867 | 14.59 | 3919 | 15.22 | 3970 | 15.85
6400 | 4076 | [36 empty] | 3926 | 15.22 | 3977 | 15.87
6600 | 4204 | [36 empty] | 3987 | 15.89
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 1825HPB
1825HPB — Backward Curved High Pressure Fan
Outlet Area: 1.92 ft² Wheel Diameter: 18.25" Tip Speed (FPM): 4.78 x RPM
Max. RPM — Design 14: 2931 Design 17: 3977 Design 22: NA Design 26: NA
CFM | OV (FPM) | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 2.5" SP |  | 3" SP |  | 3.5" SP |  | 4" SP |  | 4.5" SP |  | 5" SP |  | 5.5" SP |  | 6" SP |  | 6.5" SP |  | 7" SP |  | 7.5" SP |  | 8" SP |  | 8.5" SP |  | 9" SP |  | 9.5" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1200 | 625 | 696 | 0.14
1450 | 755 | 744 | 0.17 | 948 | 0.34
1700 | 885 | 798 | 0.21 | 984 | 0.39 | 1152 | 0.6
1950 | 1016 | 855 | 0.26 | 1030 | 0.46 | 1184 | 0.68 | 1329 | 0.93 | 1474 | 1.24
2200 | 1146 | 919 | 0.31 | 1083 | 0.53 | 1225 | 0.76 | 1359 | 1.02 | 1488 | 1.3 | 1616 | 1.64
2450 | 1276 | 990 | 0.38 | 1138 | 0.61 | 1274 | 0.86 | 1398 | 1.13 | 1518 | 1.42 | 1633 | 1.73 | 1748 | 2.09 | 1863 | 2.51
2700 | 1406 | 1063 | 0.46 | 1195 | 0.7 | 1328 | 0.98 | 1445 | 1.26 | 1556 | 1.55 | 1664 | 1.87 | 1769 | 2.21 | 1873 | 2.59 | 1978 | 3.02
2950 | 1536 | 1138 | 0.56 | 1257 | 0.8 | 1382 | 1.1 | 1497 | 1.4 | 1601 | 1.71 | 1703 | 2.04 | 1802 | 2.38 | 1899 | 2.75 | 1994 | 3.14
3200 | 1667 | 1213 | 0.66 | 1324 | 0.93 | 1438 | 1.23 | 1550 | 1.55 | 1652 | 1.88 | 1748 | 2.22 | 1842 | 2.58 | 1933 | 2.95 | 2022 | 3.34
3450 | 1797 | 1290 | 0.79 | 1395 | 1.07 | 1497 | 1.37 | 1605 | 1.72 | 1705 | 2.07 | 1798 | 2.43 | 1886 | 2.79 | 1973 | 3.18 | 2058 | 3.57 | 2142 | 3.99 | 2224 | 4.42 | 2305 | 4.87 | 2386 | 5.36 | 2468 | 5.9 | 2550 | 6.47 | 2630 | 7.06
3700 | 1927 | 1367 | 0.92 | 1468 | 1.23 | 1561 | 1.53 | 1661 | 1.89 | 1759 | 2.27 | 1850 | 2.65 | 1936 | 3.03 | 2018 | 3.42 | 2099 | 3.83 | 2179 | 4.25 | 2257 | 4.69 | 2334 | 5.14 | 2411 | 5.61 | 2486 | 6.11 | 2562 | 6.64 | 2638 | 7.21 | 2714 | 7.82 | 2789 | 8.45
3950 | 2057 | 1446 | 1.08 | 1542 | 1.4 | 1630 | 1.73 | 1720 | 2.08 | 1814 | 2.48 | 1904 | 2.88 | 1988 | 3.29 | 2068 | 3.7 | 2145 | 4.11 | 2221 | 4.55 | 2296 | 4.99 | 2370 | 5.45 | 2442 | 5.92 | 2514 | 6.41 | 2585 | 6.91 | 2656 | 7.45 | 2727 | 8.02 | 2798 | 8.62
4200 | 2188 | 1525 | 1.25 | 1617 | 1.6 | 1700 | 1.94 | 1783 | 2.3 | 1871 | 2.7 | 1959 | 3.13 | 2042 | 3.56 | 2120 | 3.99 | 2195 | 4.42 | 2267 | 4.86 | 2339 | 5.32 | 2410 | 5.79 | 2480 | 6.27 | 2549 | 6.77 | 2616 | 7.26 | 2684 | 7.79 | 2751 | 8.34 | 2817 | 8.9
4450 | 2318 | 1604 | 1.44 | 1692 | 1.81 | 1773 | 2.17 | 1850 | 2.54 | 1931 | 2.94 | 2014 | 3.38 | 2096 | 3.84 | 2174 | 4.3 | 2247 | 4.75 | 2317 | 5.2 | 2386 | 5.67 | 2454 | 6.15 | 2521 | 6.65 | 2587 | 7.15 | 2653 | 7.67 | 2717 | 8.18 | 2781 | 8.72 | 2845 | 9.28
4700 | 2448 | 1684 | 1.65 | 1769 | 2.04 | 1846 | 2.42 | 1920 | 2.81 | 1994 | 3.21 | 2072 | 3.66 | 2151 | 4.13 | 2228 | 4.61 | 2301 | 5.1 | 2370 | 5.57 | 2436 | 6.05 | 2502 | 6.55 | 2566 | 7.05 | 2630 | 7.56 | 2693 | 8.09 | 2755 | 8.62 | 2817 | 9.17 | 2878 | 9.73
4950 | 2578 | 1764 | 1.88 | 1846 | 2.3 | 1921 | 2.7 | 1992 | 3.1 | 2061 | 3.51 | 2133 | 3.96 | 2208 | 4.44 | 2282 | 4.94 | 2355 | 5.45 | 2423 | 5.95 | 2489 | 6.46 | 2553 | 6.97 | 2615 | 7.48 | 2676 | 8 | 2736 | 8.53 | 2797 | 9.09 | 2857 | 9.65 | 2916 | 10.22
5200 | 2708 | [18 empty] | 2477 | 6.35 | 2543 | 6.88 | 2605 | 7.41 | 2666 | 7.94 | 2725 | 8.47 | 2784 | 9.02 | 2842 | 9.58 | 2899 | 10.14 | 2956 | 10.72
5450 | 2839 | [18 empty] | 2532 | 6.76 | 2597 | 7.32 | 2659 | 7.87 | 2719 | 8.43 | 2777 | 8.98 | 2834 | 9.54 | 2890 | 10.11 | 2945 | 10.68 | 3000 | 11.27
5700 | 2969 | [18 empty] | 2587 | 7.18 | 2651 | 7.76 | 2713 | 8.35 | 2773 | 8.93 | 2830 | 9.5 | 2886 | 10.08 | 2941 | 10.67 | 2995 | 11.26 | 3048 | 11.86 | 3100 | 12.45 | 3153 | 13.08 | 3257 | 14.35 | 3359 | 15.64 | 3460 | 16.98 | 3559 | 18.34 | 3657 | 19.76 | 3755 | 21.26 | 3852 | 22.82
5950 | 3099 | [18 empty] | 2644 | 7.63 | 2706 | 8.23 | 2767 | 8.83 | 2827 | 9.45 | 2884 | 10.05 | 2940 | 10.66 | 2993 | 11.25 | 3046 | 11.86 | 3098 | 12.47 | 3149 | 13.09 | 3200 | 13.72 | 3300 | 15 | 3399 | 16.32 | 3497 | 17.67 | 3594 | 19.06 | 3689 | 20.48 | 3783 | 21.94 | 3877 | 23.48
6200 | 3229 | [18 empty] | 2703 | 8.11 | 2763 | 8.72 | 2822 | 9.34 | 2881 | 9.97 | 2938 | 10.6 | 2993 | 11.23 | 3047 | 11.87 | 3099 | 12.5 | 3150 | 13.13 | 3200 | 13.76 | 3249 | 14.39 | 3346 | 15.69 | 3442 | 17.03 | 3538 | 18.42 | 3631 | 19.81 | 3724 | 21.25 | 3815 | 22.71 | 3906 | 24.23
6450 | 3359 | [18 empty] | 2765 | 8.62 | 2822 | 9.24 | 2879 | 9.87 | 2936 | 10.52 | 2992 | 11.17 | 3047 | 11.83 | 3101 | 12.5 | 3152 | 13.14 | 3203 | 13.8 | 3252 | 14.45 | 3300 | 15.1 | 3395 | 16.43 | 3488 | 17.78 | 3580 | 19.17 | 3672 | 20.62 | 3762 | 22.07 | 3851 | 23.55 | 3939 | 25.06
6700 | 3490 | [18 empty] | 2830 | 9.19 | 2883 | 9.8 | 2937 | 10.43 | 2992 | 11.09 | 3047 | 11.76 | 3101 | 12.44 | 3155 | 13.13 | 3206 | 13.81 | 3257 | 14.5 | 3305 | 15.17 | 3353 | 15.85 | 3446 | 17.21 | 3537 | 18.59 | 3626 | 19.99 | 3715 | 21.44 | 3803 | 22.93 | 3890 | 24.44 | 3975 | 25.96
6950 | 3620 | [18 empty] | 2896 | 9.78 | 2947 | 10.4 | 2998 | 11.03 | 3051 | 11.7 | 3103 | 12.37 | 3156 | 13.07 | 3209 | 13.78 | 3260 | 14.49 | 3310 | 15.2 | 3359 | 15.91 | 3406 | 16.6 | 3498 | 18.01 | 3587 | 19.42 | 3675 | 20.86 | 3760 | 22.3 | 3846 | 23.81 | 3930 | 25.34
7200 | 3750 | [18 empty] | 2965 | 10.43 | 3013 | 11.04 | 3061 | 11.67 | 3111 | 12.34 | 3162 | 13.03 | 3213 | 13.74 | 3264 | 14.46 | 3314 | 15.18 | 3364 | 15.92 | 3413 | 16.66 | 3460 | 17.39 | 3552 | 18.85 | 3639 | 20.29 | 3725 | 21.76 | 3809 | 23.24 | 3891 | 24.74 | 3974 | 26.3
7450 | 3880 | [36 empty] | 3467 | 17.43 | 3514 | 18.18 | 3605 | 19.69 | 3692 | 21.19 | 3777 | 22.7 | 3859 | 24.21 | 3940 | 25.74
7700 | 4010 | [36 empty] | 3521 | 18.21 | 3568 | 18.99 | 3659 | 20.56 | 3746 | 22.12 | 3829 | 23.65 | 3910 | 25.2
7950 | 4141 | [36 empty] | 3577 | 19.03 | 3622 | 19.82 | 3713 | 21.44 | 3800 | 23.06 | 3883 | 24.66 | 3963 | 26.25
8200 | 4271 | [36 empty] | 3634 | 19.88 | 3678 | 20.69 | 3767 | 22.34 | 3853 | 24 | 3936 | 25.66
8450 | 4401 | [36 empty] | 3692 | 20.77 | 3735 | 21.59 | 3822 | 23.27 | 3907 | 24.97
8700 | 4531 | [36 empty] | 3753 | 21.72 | 3794 | 22.54 | 3878 | 24.24 | 3961 | 25.96
8950 | 4661 | [36 empty] | 3815 | 22.71 | 3855 | 23.54 | 3936 | 25.25
9200 | 4792 | [36 empty] | 3879 | 23.76 | 3917 | 24.59
9450 | 4922 | [36 empty] | 3945 | 24.88
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 2000HPB
2000HPB — Backward Curved High Pressure Fan
Outlet Area: 2.3 ft² Wheel Diameter: 20.00" Tip Speed (FPM): 5.24 x RPM
Max. RPM — Design 14: 2674 Design 17: 3629 Design 22: NA Design 26: NA
CFM | OV (FPM) | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 2.5" SP |  | 3" SP |  | 3.5" SP |  | 4" SP |  | 4.5" SP |  | 5" SP |  | 5.5" SP |  | 6" SP |  | 6.5" SP |  | 7" SP |  | 7.5" SP |  | 8" SP |  | 8.5" SP |  | 9" SP |  | 9.5" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1500 | 652 | 642 | 0.17 | 851 | 0.38
1800 | 783 | 688 | 0.21 | 870 | 0.42 | 1042 | 0.69
2100 | 913 | 738 | 0.26 | 905 | 0.48 | 1056 | 0.74 | 1203 | 1.07
2400 | 1043 | 791 | 0.32 | 949 | 0.56 | 1087 | 0.83 | 1217 | 1.13 | 1346 | 1.5
2700 | 1174 | 851 | 0.39 | 998 | 0.66 | 1126 | 0.94 | 1246 | 1.25 | 1362 | 1.59 | 1476 | 1.99
3000 | 1304 | 916 | 0.48 | 1048 | 0.75 | 1172 | 1.06 | 1284 | 1.39 | 1391 | 1.73 | 1495 | 2.11 | 1598 | 2.54 | 1701 | 3.03
3300 | 1435 | 983 | 0.58 | 1100 | 0.86 | 1221 | 1.2 | 1327 | 1.54 | 1428 | 1.9 | 1525 | 2.28 | 1620 | 2.69 | 1713 | 3.14 | 1807 | 3.65
3600 | 1565 | 1051 | 0.69 | 1158 | 0.99 | 1270 | 1.34 | 1375 | 1.72 | 1470 | 2.09 | 1562 | 2.49 | 1651 | 2.9 | 1738 | 3.34 | 1824 | 3.82
3900 | 1696 | 1120 | 0.82 | 1220 | 1.14 | 1322 | 1.5 | 1424 | 1.9 | 1517 | 2.31 | 1603 | 2.71 | 1688 | 3.14 | 1770 | 3.59 | 1851 | 4.06
4200 | 1826 | 1190 | 0.97 | 1285 | 1.32 | 1377 | 1.68 | 1474 | 2.1 | 1565 | 2.53 | 1649 | 2.96 | 1729 | 3.4 | 1808 | 3.87 | 1885 | 4.35 | 1960 | 4.84 | 2035 | 5.36 | 2108 | 5.91 | 2181 | 6.49 | 2254 | 7.12 | 2328 | 7.8 | 2401 | 8.52
4500 | 1957 | 1261 | 1.14 | 1352 | 1.51 | 1436 | 1.88 | 1525 | 2.31 | 1615 | 2.77 | 1698 | 3.23 | 1775 | 3.69 | 1850 | 4.17 | 1923 | 4.66 | 1995 | 5.17 | 2066 | 5.7 | 2136 | 6.24 | 2205 | 6.81 | 2273 | 7.4 | 2341 | 8.03 | 2409 | 8.7 | 2478 | 9.43 | 2546 | 10.18
4800 | 2087 | 1333 | 1.33 | 1420 | 1.73 | 1499 | 2.12 | 1580 | 2.55 | 1665 | 3.02 | 1747 | 3.52 | 1823 | 4.01 | 1895 | 4.5 | 1965 | 5 | 2034 | 5.53 | 2102 | 6.07 | 2169 | 6.62 | 2235 | 7.19 | 2300 | 7.77 | 2364 | 8.38 | 2428 | 9.02 | 2492 | 9.7 | 2556 | 10.41
5100 | 2217 | 1405 | 1.54 | 1488 | 1.96 | 1564 | 2.38 | 1638 | 2.81 | 1717 | 3.29 | 1797 | 3.81 | 1873 | 4.34 | 1944 | 4.86 | 2011 | 5.38 | 2077 | 5.91 | 2142 | 6.46 | 2206 | 7.03 | 2270 | 7.62 | 2332 | 8.21 | 2393 | 8.81 | 2454 | 9.44 | 2515 | 10.09 | 2575 | 10.77
5400 | 2348 | 1477 | 1.77 | 1557 | 2.22 | 1630 | 2.66 | 1700 | 3.11 | 1772 | 3.59 | 1847 | 4.12 | 1922 | 4.67 | 1993 | 5.23 | 2059 | 5.78 | 2123 | 6.33 | 2186 | 6.9 | 2247 | 7.47 | 2308 | 8.07 | 2368 | 8.68 | 2427 | 9.29 | 2486 | 9.93 | 2544 | 10.58 | 2601 | 11.24
5700 | 2478 | 1550 | 2.03 | 1627 | 2.51 | 1697 | 2.97 | 1764 | 3.44 | 1831 | 3.92 | 1901 | 4.46 | 1972 | 5.02 | 2042 | 5.61 | 2108 | 6.19 | 2171 | 6.77 | 2232 | 7.36 | 2291 | 7.95 | 2349 | 8.55 | 2407 | 9.17 | 2464 | 9.81 | 2521 | 10.46 | 2577 | 11.12 | 2632 | 11.78
6000 | 2609 | 1623 | 2.31 | 1697 | 2.82 | 1766 | 3.31 | 1829 | 3.79 | 1892 | 4.29 | 1957 | 4.82 | 2024 | 5.4 | 2092 | 6.01 | 2158 | 6.63 | 2220 | 7.23 | 2280 | 7.85 | 2338 | 8.46 | 2394 | 9.08 | 2450 | 9.71 | 2505 | 10.36 | 2559 | 11.01 | 2613 | 11.69 | 2667 | 12.38
6300 | 2739 | [18 empty] | 2270 | 7.72 | 2329 | 8.36 | 2386 | 9 | 2442 | 9.65 | 2495 | 10.28 | 2548 | 10.94 | 2601 | 11.62 | 2653 | 12.3 | 2705 | 13
6600 | 2870 | [18 empty] | 2319 | 8.2 | 2379 | 8.89 | 2435 | 9.55 | 2490 | 10.23 | 2543 | 10.9 | 2595 | 11.58 | 2645 | 12.25 | 2696 | 12.96 | 2745 | 13.65 | 2795 | 14.38 | 2844 | 15.11 | 2942 | 16.62 | 3037 | 18.15 | 3131 | 19.73 | 3224 | 21.38 | 3317 | 23.12 | 3409 | 24.95 | 3502 | 26.92
6900 | 3000 | [18 empty] | 2370 | 8.72 | 2428 | 9.42 | 2485 | 10.13 | 2539 | 10.83 | 2592 | 11.54 | 2642 | 12.23 | 2692 | 12.94 | 2741 | 13.65 | 2789 | 14.36 | 2837 | 15.1 | 2884 | 15.83 | 2979 | 17.37 | 3072 | 18.94 | 3163 | 20.53 | 3253 | 22.18 | 3342 | 23.88 | 3431 | 25.68 | 3519 | 27.54
7200 | 3130 | [18 empty] | 2422 | 9.26 | 2478 | 9.98 | 2534 | 10.71 | 2588 | 11.45 | 2641 | 12.19 | 2691 | 12.92 | 2740 | 13.65 | 2788 | 14.38 | 2835 | 15.11 | 2882 | 15.87 | 2928 | 16.62 | 3018 | 18.15 | 3109 | 19.76 | 3198 | 21.39 | 3285 | 23.04 | 3372 | 24.76 | 3457 | 26.51 | 3542 | 28.34
7500 | 3261 | [18 empty] | 2477 | 9.85 | 2530 | 10.57 | 2584 | 11.32 | 2638 | 12.09 | 2690 | 12.86 | 2740 | 13.62 | 2789 | 14.39 | 2836 | 15.14 | 2883 | 15.91 | 2928 | 16.66 | 2973 | 17.44 | 3061 | 19 | 3148 | 20.61 | 3235 | 22.28 | 3320 | 23.97 | 3404 | 25.69 | 3487 | 27.45 | 3569 | 29.26
7800 | 3391 | [18 empty] | 2534 | 10.48 | 2585 | 11.21 | 2636 | 11.97 | 2688 | 12.75 | 2739 | 13.54 | 2789 | 14.33 | 2838 | 15.13 | 2885 | 15.92 | 2931 | 16.72 | 2976 | 17.51 | 3020 | 18.3 | 3106 | 19.89 | 3191 | 21.53 | 3274 | 23.2 | 3357 | 24.92 | 3439 | 26.68 | 3520 | 28.47 | 3600 | 30.29
8100 | 3522 | [18 empty] | 2593 | 11.16 | 2641 | 11.89 | 2690 | 12.65 | 2740 | 13.45 | 2789 | 14.25 | 2839 | 15.08 | 2887 | 15.9 | 2935 | 16.74 | 2980 | 17.55 | 3025 | 18.38 | 3068 | 19.19 | 3153 | 20.83 | 3235 | 22.49 | 3316 | 24.18 | 3397 | 25.93 | 3477 | 27.72 | 3556 | 29.54
8400 | 3652 | [18 empty] | 2654 | 11.88 | 2699 | 12.61 | 2746 | 13.39 | 2793 | 14.18 | 2841 | 15 | 2889 | 15.84 | 2937 | 16.7 | 2984 | 17.56 | 3029 | 18.4 | 3074 | 19.27 | 3117 | 20.11 | 3201 | 21.81 | 3282 | 23.51 | 3361 | 25.23 | 3439 | 26.99 | 3516 | 28.78 | 3593 | 30.63
8700 | 3783 | [18 empty] | 2717 | 12.67 | 2760 | 13.4 | 2804 | 14.17 | 2849 | 14.97 | 2895 | 15.8 | 2941 | 16.64 | 2987 | 17.51 | 3033 | 18.39 | 3078 | 19.27 | 3123 | 20.17 | 3166 | 21.05 | 3249 | 22.8 | 3329 | 24.55 | 3407 | 26.32 | 3483 | 28.1 | 3559 | 29.93
9000 | 3913 | [36 empty] | 3172 | 21.09 | 3215 | 22 | 3298 | 23.83 | 3378 | 25.65 | 3455 | 27.47 | 3529 | 29.27 | 3603 | 31.13
9300 | 4043 | [36 empty] | 3222 | 22.04 | 3264 | 22.97 | 3347 | 24.87 | 3427 | 26.76 | 3503 | 28.63 | 3577 | 30.5
9600 | 4174 | [36 empty] | 3273 | 23.03 | 3314 | 23.98 | 3396 | 25.92 | 3476 | 27.89 | 3551 | 29.81 | 3625 | 31.75
9900 | 4304 | [36 empty] | 3325 | 24.06 | 3365 | 25.02 | 3446 | 27.02 | 3524 | 29.02 | 3600 | 31.02
10200 | 4435 | [36 empty] | 3379 | 25.15 | 3418 | 26.13 | 3496 | 28.14 | 3574 | 30.21
10500 | 4565 | [36 empty] | 3434 | 26.28 | 3472 | 27.28 | 3547 | 29.3 | 3623 | 31.39
10800 | 4696 | [36 empty] | 3491 | 27.49 | 3527 | 28.48 | 3600 | 30.52
11100 | 4826 | [36 empty] | 3550 | 28.77 | 3585 | 29.77
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 2225HPB
2225HPB — Backward Curved High Pressure Fan
Outlet Area: 2.85 ft² Wheel Diameter: 22.25" Tip Speed (FPM): 5.83 x RPM
Max. RPM — Design 14: 2404 Design 17: 3262 Design 22: 3777 Design 26: NA
CFM | OV (FPM) | 1" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP |  | 21" SP |  | 22" SP |  | 23" SP |  | 24" SP |  | 25" SP |  | 26" SP |  | 27" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1800 | 632 | 731 | 0.41
2200 | 772 | 753 | 0.49
2600 | 912 | 783 | 0.57 | 1036 | 1.19
3000 | 1053 | 823 | 0.67 | 1057 | 1.33
3400 | 1193 | 868 | 0.78 | 1084 | 1.49 | 1279 | 2.3
3800 | 1333 | 917 | 0.91 | 1118 | 1.66 | 1302 | 2.51 | 1469 | 3.44
4200 | 1474 | 970 | 1.06 | 1158 | 1.86 | 1330 | 2.75 | 1491 | 3.72 | 1640 | 4.77
4600 | 1614 | 1025 | 1.23 | 1202 | 2.08 | 1364 | 3.02 | 1517 | 4.03 | 1661 | 5.12 | 1796 | 6.27
5000 | 1754 | 1082 | 1.42 | 1249 | 2.32 | 1403 | 3.31 | 1547 | 4.37 | 1685 | 5.49 | 1816 | 6.68 | 1940 | 7.92
5400 | 1895 | 1140 | 1.63 | 1300 | 2.59 | 1445 | 3.62 | 1582 | 4.72 | 1714 | 5.9 | 1840 | 7.12 | 1961 | 8.41 | 2076 | 9.75 | 2186 | 11.13
5800 | 2035 | 1200 | 1.86 | 1352 | 2.89 | 1490 | 3.96 | 1621 | 5.11 | 1747 | 6.33 | 1868 | 7.6 | 1984 | 8.92 | 2097 | 10.31 | 2204 | 11.73 | 2308 | 13.21
6200 | 2175 | 1261 | 2.12 | 1406 | 3.21 | 1539 | 4.34 | 1664 | 5.53 | 1783 | 6.78 | 1899 | 8.11 | 2012 | 9.48 | 2120 | 10.88 | 2225 | 12.35 | 2327 | 13.88 | 2425 | 15.44 | 2520 | 17.04
6600 | 2316 | 1324 | 2.42 | 1462 | 3.56 | 1589 | 4.74 | 1709 | 5.98 | 1824 | 7.29 | 1934 | 8.64 | 2042 | 10.06 | 2147 | 11.51 | 2250 | 13.04 | 2348 | 14.57 | 2444 | 16.18 | 2537 | 17.82 | 2628 | 19.52
7000 | 2456 | 1388 | 2.74 | 1518 | 3.93 | 1641 | 5.18 | 1756 | 6.46 | 1867 | 7.82 | 1973 | 9.22 | 2077 | 10.69 | 2178 | 12.19 | 2277 | 13.74 | 2373 | 15.33 | 2466 | 16.96 | 2557 | 18.64 | 2646 | 20.38 | 2732 | 22.13 | 2817 | 23.94
7400 | 2596 | 1453 | 3.11 | 1576 | 4.34 | 1695 | 5.65 | 1805 | 6.98 | 1912 | 8.38 | 2014 | 9.82 | 2114 | 11.33 | 2211 | 12.88 | 2307 | 14.49 | 2400 | 16.12 | 2491 | 17.79 | 2580 | 19.51 | 2667 | 21.28 | 2751 | 23.07 | 2834 | 24.92 | 2915 | 26.8 | 2994 | 28.7
7800 | 2737 | 1518 | 3.5 | 1635 | 4.78 | 1750 | 6.15 | 1857 | 7.55 | 1959 | 8.98 | 2058 | 10.47 | 2154 | 12.02 | 2248 | 13.62 | 2340 | 15.27 | 2430 | 16.94 | 2519 | 18.67 | 2605 | 20.41 | 2690 | 22.22 | 2773 | 24.06 | 2854 | 25.94 | 2933 | 27.85 | 3011 | 29.81 | 3087 | 31.78
8200 | 2877 | [18 empty] | 2463 | 17.81 | 2549 | 19.58 | 2633 | 21.38 | 2716 | 23.22 | 2797 | 25.09 | 2876 | 27 | 2954 | 28.96 | 3030 | 30.94 | 3105 | 32.97
8600 | 3018 | [18 empty] | 2499 | 18.71 | 2582 | 20.53 | 2664 | 22.39 | 2744 | 24.26 | 2823 | 26.17 | 2901 | 28.13 | 2977 | 30.11 | 3052 | 32.14 | 3125 | 34.2
9000 | 3158 | [18 empty] | 2538 | 19.68 | 2618 | 21.53 | 2697 | 23.42 | 2775 | 25.35 | 2852 | 27.31 | 2928 | 29.31 | 3002 | 31.32 | 3076 | 33.4 | 3148 | 35.49 | 3218 | 37.6 | 3288 | 39.78 | 3356 | 41.96 | 3424 | 44.21 | 3490 | 46.44 | 3556 | 48.74 | 3620 | 51.02
9400 | 3298 | [18 empty] | 2579 | 20.68 | 2656 | 22.56 | 2733 | 24.51 | 2809 | 26.5 | 2883 | 28.49 | 2957 | 30.53 | 3030 | 32.6 | 3101 | 34.68 | 3172 | 36.82 | 3242 | 39 | 3310 | 41.19 | 3377 | 43.41 | 3443 | 45.67 | 3509 | 47.99 | 3573 | 50.29 | 3636 | 52.62 | 3699 | 55 | 3761 | 57.41
9800 | 3439 | [18 empty] | 2621 | 21.72 | 2697 | 23.67 | 2771 | 25.64 | 2845 | 27.67 | 2917 | 29.71 | 2989 | 31.81 | 3059 | 33.9 | 3129 | 36.04 | 3199 | 38.24 | 3267 | 40.44 | 3334 | 42.66 | 3400 | 44.92 | 3465 | 47.22 | 3529 | 49.54 | 3592 | 51.89 | 3655 | 54.3 | 3716 | 56.68 | 3777 | 59.12
10200 | 3579 | [18 empty] | 2665 | 22.81 | 2739 | 24.81 | 2811 | 26.82 | 2883 | 28.9 | 2953 | 30.98 | 3023 | 33.12 | 3092 | 35.29 | 3160 | 37.47 | 3227 | 39.67 | 3294 | 41.93 | 3359 | 44.17 | 3424 | 46.47 | 3488 | 48.8 | 3552 | 51.2 | 3614 | 53.58 | 3675 | 55.99 | 3736 | 58.45
10600 | 3719 | [18 empty] | 2711 | 23.97 | 2783 | 26.01 | 2853 | 28.06 | 2923 | 30.17 | 2991 | 32.29 | 3059 | 34.47 | 3126 | 36.68 | 3192 | 38.91 | 3258 | 41.18 | 3323 | 43.47 | 3387 | 45.77 | 3451 | 48.12 | 3514 | 50.5 | 3576 | 52.89 | 3637 | 55.3 | 3697 | 57.74 | 3757 | 60.24
11000 | 3860 | [18 empty] | 2758 | 25.18 | 2828 | 27.25 | 2897 | 29.36 | 2965 | 31.52 | 3031 | 33.67 | 3097 | 35.88 | 3163 | 38.16 | 3227 | 40.42 | 3291 | 42.73 | 3354 | 45.05 | 3417 | 47.42 | 3479 | 49.79 | 3541 | 52.22 | 3602 | 54.66 | 3662 | 57.11 | 3721 | 59.58
11400 | 4000 | [18 empty] | 2806 | 26.43 | 2874 | 28.54 | 2942 | 30.72 | 3008 | 32.9 | 3073 | 35.12 | 3137 | 37.36 | 3201 | 39.66 | 3264 | 41.99 | 3326 | 44.33 | 3388 | 46.72 | 3449 | 49.12 | 3510 | 51.56 | 3570 | 54.01 | 3629 | 56.45 | 3688 | 58.95 | 3747 | 61.51
11800 | 4140 | [18 empty] | 2856 | 27.77 | 2922 | 29.91 | 2988 | 32.12 | 3052 | 34.33 | 3116 | 36.6 | 3179 | 38.91 | 3241 | 41.24 | 3302 | 43.58 | 3363 | 45.98 | 3423 | 48.4 | 3483 | 50.86 | 3542 | 53.33 | 3601 | 55.84 | 3659 | 58.35 | 3717 | 60.91 | 3774 | 63.46
12200 | 4281 | [36 empty] | 3461 | 50.19 | 3519 | 52.67 | 3577 | 55.2 | 3634 | 57.73 | 3691 | 60.31 | 3747 | 62.87
12600 | 4421 | [36 empty] | 3500 | 52.01 | 3557 | 54.55 | 3613 | 57.09 | 3669 | 59.68 | 3724 | 62.27
13000 | 4561 | [36 empty] | 3540 | 53.88 | 3596 | 56.47 | 3651 | 59.06 | 3706 | 61.71 | 3760 | 64.35
13400 | 4702 | [36 empty] | 3582 | 55.85 | 3637 | 58.49 | 3691 | 61.13 | 3744 | 63.77
13800 | 4842 | [36 empty] | 3625 | 57.87 | 3679 | 60.56 | 3731 | 63.2
14200 | 4982 | [36 empty] | 3669 | 59.95 | 3722 | 62.69 | 3773 | 65.37
14600 | 5123 | [36 empty] | 3715 | 62.15 | 3766 | 64.88
15000 | 5263 | [36 empty] | 3761 | 64.38
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 2450HPB
2450HPB — Backward Curved High Pressure Fan
Outlet Area: 3.45 ft² Wheel Diameter: 24.50" Tip Speed (FPM): 6.41 x RPM
Max. RPM — Design 14: 2183 Design 17: 2963 Design 22: 3560 Design 26: NA
CFM | OV (FPM) | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP |  | 21" SP |  | 22" SP |  | 23" SP |  | 24" SP |  | 25" SP |  | 26" SP |  | 27" SP |  | 28" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3500 | 1014 | 954 | 1.56
4000 | 1159 | 978 | 1.75 | 1157 | 2.72
4500 | 1304 | 1008 | 1.97 | 1177 | 2.98 | 1331 | 4.1
5000 | 1449 | 1045 | 2.21 | 1203 | 3.28 | 1350 | 4.45 | 1486 | 5.7
5500 | 1594 | 1085 | 2.48 | 1233 | 3.6 | 1373 | 4.82 | 1505 | 6.13 | 1628 | 7.51
6000 | 1739 | 1129 | 2.78 | 1269 | 3.96 | 1401 | 5.24 | 1527 | 6.59 | 1647 | 8.03 | 1760 | 9.54
6500 | 1884 | 1176 | 3.11 | 1308 | 4.34 | 1434 | 5.69 | 1554 | 7.1 | 1669 | 8.58 | 1779 | 10.14 | 1883 | 11.75 | 1984 | 13.43
7000 | 2029 | 1225 | 3.48 | 1351 | 4.78 | 1470 | 6.16 | 1584 | 7.63 | 1694 | 9.17 | 1801 | 10.78 | 1903 | 12.45 | 2001 | 14.18 | 2095 | 15.96
7500 | 2174 | 1275 | 3.87 | 1396 | 5.24 | 1510 | 6.69 | 1618 | 8.2 | 1724 | 9.81 | 1826 | 11.46 | 1925 | 13.18 | 2020 | 14.95 | 2112 | 16.79 | 2202 | 18.7 | 2288 | 20.63
8000 | 2319 | 1327 | 4.31 | 1443 | 5.75 | 1552 | 7.25 | 1656 | 8.83 | 1757 | 10.48 | 1855 | 12.2 | 1950 | 13.96 | 2043 | 15.79 | 2133 | 17.68 | 2220 | 19.63 | 2304 | 21.61 | 2386 | 23.64
8500 | 2464 | 1380 | 4.78 | 1492 | 6.3 | 1596 | 7.85 | 1696 | 9.49 | 1793 | 11.2 | 1887 | 12.97 | 1978 | 14.79 | 2068 | 16.67 | 2156 | 18.62 | 2241 | 20.61 | 2323 | 22.64 | 2403 | 24.72 | 2482 | 26.88 | 2559 | 29.07
9000 | 2609 | 1434 | 5.28 | 1542 | 6.88 | 1642 | 8.5 | 1738 | 10.19 | 1832 | 11.97 | 1922 | 13.79 | 2010 | 15.67 | 2097 | 17.63 | 2181 | 19.6 | 2264 | 21.64 | 2345 | 23.74 | 2423 | 25.86 | 2500 | 28.06 | 2575 | 30.29 | 2648 | 32.56 | 2720 | 34.88
9500 | 2754 | 1490 | 5.84 | 1594 | 7.52 | 1690 | 9.21 | 1783 | 10.96 | 1873 | 12.78 | 1960 | 14.66 | 2045 | 16.6 | 2128 | 18.6 | 2210 | 20.65 | 2290 | 22.74 | 2368 | 24.85 | 2445 | 27.04 | 2520 | 29.27 | 2594 | 31.58 | 2665 | 33.88 | 2736 | 36.26 | 2805 | 38.67 | 2873 | 41.12
10000 | 2899 | 1546 | 6.44 | 1646 | 8.19 | 1740 | 9.97 | 1829 | 11.77 | 1915 | 13.63 | 2000 | 15.58 | 2082 | 17.58 | 2162 | 19.62 | 2241 | 21.73 | 2318 | 23.87 | 2395 | 26.08 | 2470 | 28.32 | 2543 | 30.58 | 2615 | 32.91 | 2685 | 35.27 | 2754 | 37.69 | 2822 | 40.16 | 2888 | 42.63
10500 | 3043 | 1603 | 7.09 | 1699 | 8.9 | 1790 | 10.76 | 1877 | 12.64 | 1960 | 14.56 | 2042 | 16.56 | 2121 | 18.6 | 2199 | 20.72 | 2275 | 22.87 | 2350 | 25.08 | 2424 | 27.34 | 2496 | 29.61 | 2568 | 31.95 | 2638 | 34.31 | 2707 | 36.73 | 2775 | 39.2 | 2841 | 41.69 | 2906 | 44.23
11000 | 3188 | 1662 | 7.8 | 1753 | 9.66 | 1842 | 11.61 | 1926 | 13.57 | 2007 | 15.56 | 2085 | 17.58 | 2162 | 19.69 | 2238 | 21.87 | 2311 | 24.06 | 2384 | 26.33 | 2455 | 28.63 | 2526 | 31 | 2595 | 33.37 | 2664 | 35.81 | 2731 | 38.26 | 2797 | 40.75 | 2863 | 43.33 | 2927 | 45.92 | 2989 | 48.51 | 3051 | 51.18 | 3112 | 53.89 | 3172 | 56.62 | 3232 | 59.43 | 3290 | 62.21 | 3348 | 65.07
11500 | 3333 | [18 empty] | 2420 | 27.64 | 2489 | 29.99 | 2557 | 32.39 | 2625 | 34.87 | 2691 | 37.32 | 2757 | 39.85 | 2822 | 42.41 | 2886 | 45.02 | 2949 | 47.66
12000 | 3478 | [18 empty] | 2458 | 29.01 | 2525 | 31.42 | 2592 | 33.91 | 2657 | 36.4 | 2721 | 38.92 | 2785 | 41.5 | 2849 | 44.14 | 2911 | 46.77 | 2972 | 49.42 | 3033 | 52.16 | 3093 | 54.92 | 3152 | 57.72 | 3210 | 60.56 | 3267 | 63.42 | 3323 | 66.29 | 3379 | 69.24 | 3434 | 72.2 | 3489 | 75.24
12500 | 3623 | [18 empty] | 2498 | 30.46 | 2563 | 32.91 | 2628 | 35.45 | 2691 | 37.99 | 2754 | 40.6 | 2816 | 43.23 | 2877 | 45.88 | 2938 | 48.59 | 2998 | 51.31 | 3058 | 54.11 | 3116 | 56.88 | 3174 | 59.72 | 3231 | 62.59 | 3288 | 65.55 | 3343 | 68.47 | 3398 | 71.46 | 3452 | 74.47 | 3505 | 77.48
13000 | 3768 | [18 empty] | 2539 | 31.96 | 2603 | 34.49 | 2666 | 37.07 | 2728 | 39.69 | 2789 | 42.34 | 2849 | 45.02 | 2909 | 47.76 | 2968 | 50.51 | 3026 | 53.27 | 3084 | 56.09 | 3142 | 58.98 | 3198 | 61.82 | 3254 | 64.74 | 3310 | 67.73 | 3364 | 70.68 | 3418 | 73.71 | 3471 | 76.75 | 3524 | 79.87
13500 | 3913 | [18 empty] | 2582 | 33.55 | 2644 | 36.12 | 2705 | 38.74 | 2766 | 41.44 | 2825 | 44.12 | 2884 | 46.87 | 2942 | 49.65 | 2999 | 52.44 | 3056 | 55.29 | 3113 | 58.19 | 3169 | 61.1 | 3224 | 64.01 | 3279 | 66.98 | 3333 | 69.96 | 3387 | 73.01 | 3440 | 76.07 | 3493 | 79.21 | 3544 | 82.29
14000 | 4058 | [18 empty] | 2626 | 35.2 | 2687 | 37.86 | 2746 | 40.51 | 2805 | 43.23 | 2863 | 45.99 | 2920 | 48.77 | 2977 | 51.62 | 3033 | 54.49 | 3088 | 57.37 | 3143 | 60.3 | 3198 | 63.29 | 3252 | 66.27 | 3306 | 69.31 | 3359 | 72.35 | 3412 | 75.46 | 3464 | 78.56 | 3515 | 81.66
14500 | 4203 | [18 empty] | 2672 | 36.97 | 2730 | 39.61 | 2788 | 42.33 | 2846 | 45.13 | 2902 | 47.91 | 2958 | 50.77 | 3014 | 53.69 | 3068 | 56.57 | 3122 | 59.52 | 3176 | 62.53 | 3229 | 65.55 | 3282 | 68.61 | 3334 | 71.66 | 3386 | 74.77 | 3438 | 77.93 | 3489 | 81.09 | 3540 | 84.3
15000 | 4348 | [18 empty] | 2718 | 38.78 | 2775 | 41.49 | 2832 | 44.28 | 2888 | 47.1 | 2943 | 49.95 | 2998 | 52.87 | 3052 | 55.81 | 3105 | 58.76 | 3158 | 61.78 | 3210 | 64.8 | 3262 | 67.88 | 3314 | 71.02 | 3365 | 74.15 | 3415 | 77.27 | 3466 | 80.5 | 3516 | 83.71
15500 | 4493 | [36 empty] | 3246 | 67.17 | 3297 | 70.32 | 3347 | 73.46 | 3397 | 76.66 | 3447 | 79.91 | 3496 | 83.15 | 3545 | 86.43
16000 | 4638 | [36 empty] | 3284 | 69.67 | 3333 | 72.81 | 3382 | 76.01 | 3431 | 79.27 | 3479 | 82.51 | 3527 | 85.81
16500 | 4783 | [36 empty] | 3322 | 72.16 | 3371 | 75.43 | 3419 | 78.68 | 3466 | 81.93 | 3514 | 85.3
17000 | 4928 | [36 empty] | 3362 | 74.8 | 3410 | 78.12 | 3457 | 81.43 | 3503 | 84.72 | 3550 | 88.15
17500 | 5072 | [36 empty] | 3403 | 77.52 | 3450 | 80.89 | 3496 | 84.25 | 3541 | 87.59
18000 | 5217 | [36 empty] | 3445 | 80.34 | 3491 | 83.75 | 3536 | 87.16
18500 | 5362 | [36 empty] | 3488 | 83.25 | 3533 | 86.71
19000 | 5507 | [36 empty] | 3532 | 86.27
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 2700HPB
2700HPB — Backward Curved High Pressure Fan
Outlet Area: 4.19 ft² Wheel Diameter: 27.00" Tip Speed (FPM): 7.07 x RPM
Max. RPM — Design 14: 1981 Design 17: 2687 Design 22: 3112 Design 26: 3678
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
6000 | 1432 | 902 | 2.41 | 1185 | 4.94
6500 | 1551 | 926 | 2.62 | 1197 | 5.26
7000 | 1671 | 954 | 2.87 | 1212 | 5.6 | 1444 | 8.74
7500 | 1790 | 983 | 3.14 | 1231 | 5.98 | 1453 | 9.19
8000 | 1909 | 1014 | 3.43 | 1252 | 6.39 | 1465 | 9.67 | 1665 | 13.34
8500 | 2029 | 1047 | 3.76 | 1274 | 6.79 | 1481 | 10.21 | 1673 | 13.93
9000 | 2148 | 1081 | 4.11 | 1299 | 7.24 | 1499 | 10.76 | 1684 | 14.56 | 1860 | 18.68
9500 | 2267 | 1116 | 4.48 | 1325 | 7.7 | 1519 | 11.35 | 1698 | 15.23 | 1869 | 19.45
10000 | 2387 | 1153 | 4.9 | 1353 | 8.2 | 1540 | 11.94 | 1715 | 15.96 | 1880 | 20.24 | 2038 | 24.77
10500 | 2506 | 1190 | 5.35 | 1382 | 8.73 | 1563 | 12.57 | 1733 | 16.7 | 1893 | 21.05 | 2047 | 25.69 | 2195 | 30.55
11000 | 2625 | 1228 | 5.83 | 1413 | 9.31 | 1587 | 13.21 | 1753 | 17.48 | 1909 | 21.94 | 2058 | 26.63 | 2203 | 31.61
11500 | 2745 | 1267 | 6.35 | 1444 | 9.91 | 1613 | 13.91 | 1774 | 18.27 | 1926 | 22.83 | 2072 | 27.64 | 2212 | 32.66 | 2349 | 37.94
12000 | 2864 | 1307 | 6.91 | 1477 | 10.57 | 1640 | 14.63 | 1797 | 19.11 | 1946 | 23.82 | 2087 | 28.66 | 2224 | 33.78 | 2357 | 39.13 | 2486 | 44.66
12500 | 2983 | 1346 | 7.49 | 1511 | 11.26 | 1669 | 15.42 | 1821 | 19.97 | 1966 | 24.78 | 2104 | 29.74 | 2238 | 34.96 | 2367 | 40.35 | 2494 | 46.02 | 2617 | 51.85
13000 | 3103 | 1387 | 8.13 | 1546 | 12 | 1699 | 16.25 | 1846 | 20.86 | 1988 | 25.8 | 2123 | 30.89 | 2253 | 36.15 | 2380 | 41.67 | 2503 | 47.37 | 2624 | 53.31 | 2741 | 59.39
13500 | 3222 | 1427 | 8.78 | 1581 | 12.76 | 1729 | 17.09 | 1872 | 21.79 | 2011 | 26.85 | 2143 | 32.05 | 2271 | 37.46 | 2394 | 43 | 2514 | 48.77 | 2632 | 54.78 | 2747 | 60.94
14000 | 3341 | [18 empty] | 2642 | 56.3 | 2755 | 62.57 | 2865 | 68.97
14500 | 3461 | [18 empty] | 2655 | 57.95 | 2765 | 64.27 | 2873 | 70.76 | 2979 | 77.43 | 3031 | 80.82
15000 | 3580 | [18 empty] | 2669 | 59.62 | 2776 | 65.97 | 2882 | 72.56 | 2986 | 79.3 | 3037 | 82.72 | 3088 | 86.21 | 3138 | 89.7
15500 | 3699 | [18 empty] | 2684 | 61.32 | 2789 | 67.75 | 2893 | 74.44 | 2995 | 81.27 | 3045 | 84.71 | 3095 | 88.23 | 3145 | 91.83 | 3193 | 95.33 | 3242 | 99.01
16000 | 3819 | [18 empty] | 2701 | 63.13 | 2804 | 69.64 | 2905 | 76.32 | 3005 | 83.25 | 3055 | 86.81 | 3104 | 90.36 | 3152 | 93.9 | 3200 | 97.51 | 3248 | 101.19 | 3295 | 104.86 | 3342 | 108.61
16500 | 3938 | [18 empty] | 2719 | 64.97 | 2820 | 71.57 | 2920 | 78.4 | 3017 | 85.31 | 3065 | 88.83 | 3114 | 92.51 | 3161 | 96.07 | 3209 | 99.8 | 3256 | 103.5 | 3302 | 107.18 | 3348 | 110.93 | 3394 | 114.76 | 3439 | 118.56
17000 | 4057 | [18 empty] | 2738 | 66.87 | 2837 | 73.54 | 2935 | 80.44 | 3031 | 87.48 | 3078 | 91.03 | 3125 | 94.66 | 3172 | 98.35 | 3218 | 102.01 | 3264 | 105.74 | 3310 | 109.53 | 3356 | 113.4 | 3401 | 117.23 | 3445 | 121.03 | 3490 | 125.01 | 3533 | 128.84
17500 | 4177 | [18 empty] | 2758 | 68.8 | 2856 | 75.64 | 2952 | 82.61 | 3046 | 89.7 | 3092 | 93.27 | 3138 | 96.91 | 3184 | 100.63 | 3229 | 104.33 | 3275 | 108.19 | 3320 | 112 | 3364 | 115.78 | 3409 | 119.73 | 3453 | 123.64 | 3496 | 127.51 | 3540 | 131.55 | 3583 | 135.56 | 3625 | 139.53
18000 | 4296 | [18 empty] | 2779 | 70.78 | 2875 | 77.71 | 2969 | 84.74 | 3062 | 91.98 | 3107 | 95.56 | 3153 | 99.32 | 3197 | 102.96 | 3242 | 106.76 | 3286 | 110.54 | 3330 | 114.39 | 3374 | 118.29 | 3418 | 122.26 | 3461 | 126.17 | 3504 | 130.15 | 3547 | 134.2 | 3589 | 138.2 | 3631 | 142.26 | 3673 | 146.4
18500 | 4415 | [18 empty] | 2800 | 72.74 | 2895 | 79.83 | 2988 | 87.02 | 3079 | 94.31 | 3124 | 98.01 | 3168 | 101.69 | 3212 | 105.43 | 3256 | 109.25 | 3300 | 113.13 | 3343 | 116.99 | 3386 | 120.92 | 3428 | 124.8 | 3471 | 128.84 | 3513 | 132.83 | 3555 | 136.88 | 3597 | 140.99 | 3639 | 145.17
19000 | 4535 | [18 empty] | 2823 | 74.83 | 2916 | 82 | 3007 | 89.26 | 3097 | 96.7 | 3141 | 100.42 | 3185 | 104.21 | 3228 | 107.97 | 3271 | 111.79 | 3314 | 115.69 | 3356 | 119.55 | 3399 | 123.58 | 3441 | 127.58 | 3482 | 131.53 | 3524 | 135.65 | 3565 | 139.71 | 3606 | 143.82 | 3647 | 147.99
19500 | 4654 | [18 empty] | 2846 | 76.9 | 2938 | 84.23 | 3028 | 91.65 | 3116 | 99.14 | 3159 | 102.89 | 3202 | 106.7 | 3245 | 110.57 | 3288 | 114.51 | 3330 | 118.41 | 3371 | 122.27 | 3413 | 126.31 | 3454 | 130.3 | 3495 | 134.36 | 3536 | 138.48 | 3576 | 142.55 | 3616 | 146.67 | 3657 | 150.97
20000 | 4773 | [18 empty] | 2870 | 79.05 | 2960 | 86.44 | 3049 | 94.01 | 3136 | 101.66 | 3179 | 105.52 | 3221 | 109.35 | 3263 | 113.24 | 3305 | 117.19 | 3346 | 121.1 | 3387 | 125.07 | 3428 | 129.1 | 3469 | 133.2 | 3509 | 137.25 | 3549 | 141.37 | 3589 | 145.55 | 3628 | 149.67 | 3668 | 153.98
20500 | 4893 | [36 empty] | 3404 | 127.94 | 3444 | 131.97 | 3484 | 136.07 | 3524 | 140.22 | 3563 | 144.33 | 3602 | 148.49 | 3641 | 152.72
21000 | 5012 | [36 empty] | 3422 | 130.88 | 3462 | 135.03 | 3501 | 139.13 | 3540 | 143.28 | 3579 | 147.49 | 3617 | 151.64 | 3655 | 155.85
21500 | 5131 | [36 empty] | 3441 | 133.91 | 3480 | 138.06 | 3518 | 142.14 | 3557 | 146.41 | 3595 | 150.61 | 3633 | 154.87 | 3671 | 159.19
22000 | 5251 | [36 empty] | 3460 | 136.89 | 3498 | 141.04 | 3537 | 145.37 | 3574 | 149.51 | 3612 | 153.82 | 3650 | 158.2
23000 | 5489 | [36 empty] | 3501 | 143.12 | 3538 | 147.39 | 3576 | 151.83 | 3612 | 156.08 | 3649 | 160.5
24000 | 5728 | [36 empty] | 3544 | 149.46 | 3581 | 153.97 | 3617 | 158.41 | 3653 | 162.89
25000 | 5967 | [36 empty] | 3590 | 156.1 | 3626 | 160.71 | 3661 | 165.25
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 3000HPB
3000HPB — Backward Curved High Pressure Fan
Outlet Area: 5.17 ft² Wheel Diameter: 30.00" Tip Speed (FPM): 7.85 x RPM
Max. RPM — Design 14: 1783 Design 17: 2420 Design 22: 2801 Design 26: 3310
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
7500 | 1451 | 815 | 3.01 | 1068 | 6.15
8000 | 1547 | 833 | 3.23 | 1077 | 6.48
8500 | 1644 | 852 | 3.46 | 1088 | 6.83 | 1298 | 10.66
9000 | 1741 | 873 | 3.72 | 1101 | 7.2 | 1304 | 11.11
9500 | 1838 | 895 | 4 | 1115 | 7.58 | 1312 | 11.59
10000 | 1934 | 919 | 4.32 | 1130 | 7.97 | 1321 | 12.06 | 1500 | 16.62
10500 | 2031 | 943 | 4.65 | 1147 | 8.39 | 1333 | 12.6 | 1506 | 17.22
11000 | 2128 | 967 | 4.98 | 1165 | 8.83 | 1346 | 13.16 | 1514 | 17.85 | 1673 | 22.9
11500 | 2224 | 993 | 5.37 | 1183 | 9.27 | 1360 | 13.73 | 1523 | 18.48 | 1679 | 23.66
12000 | 2321 | 1019 | 5.76 | 1203 | 9.76 | 1375 | 14.33 | 1535 | 19.21 | 1686 | 24.43 | 1831 | 29.99
12500 | 2418 | 1046 | 6.19 | 1224 | 10.28 | 1391 | 14.93 | 1547 | 19.92 | 1694 | 25.2 | 1836 | 30.86
13000 | 2515 | 1073 | 6.64 | 1245 | 10.81 | 1408 | 15.57 | 1561 | 20.69 | 1705 | 26.07 | 1843 | 31.79 | 1976 | 37.8
13500 | 2611 | 1101 | 7.12 | 1268 | 11.4 | 1426 | 16.23 | 1575 | 21.45 | 1716 | 26.93 | 1851 | 32.73 | 1982 | 38.87
14000 | 2708 | 1129 | 7.63 | 1291 | 12.01 | 1444 | 16.89 | 1591 | 22.27 | 1729 | 27.86 | 1860 | 33.69 | 1988 | 39.9 | 2112 | 46.38
14500 | 2805 | 1158 | 8.17 | 1314 | 12.62 | 1464 | 17.62 | 1607 | 23.08 | 1742 | 28.78 | 1871 | 34.72 | 1996 | 41 | 2117 | 47.53 | 2235 | 54.36
15000 | 2901 | 1187 | 8.75 | 1339 | 13.31 | 1484 | 18.36 | 1624 | 23.92 | 1756 | 29.73 | 1883 | 35.8 | 2005 | 42.12 | 2124 | 48.77 | 2240 | 55.68
16000 | 3095 | [18 empty] | 2361 | 65.67
17000 | 3288 | [18 empty] | 2374 | 68.68 | 2476 | 76.31 | 2576 | 84.19
18000 | 3482 | [18 empty] | 2391 | 71.83 | 2490 | 79.68 | 2587 | 87.72 | 2682 | 95.96 | 2729 | 100.18
19000 | 3675 | [18 empty] | 2412 | 75.18 | 2508 | 83.21 | 2601 | 91.35 | 2694 | 99.84 | 2739 | 104.06 | 2784 | 108.37 | 2829 | 112.79 | 2873 | 117.18
20000 | 3868 | [18 empty] | 2437 | 78.81 | 2529 | 86.89 | 2620 | 95.27 | 2709 | 103.82 | 2753 | 108.17 | 2797 | 112.61 | 2840 | 117.01 | 2883 | 121.49 | 2926 | 126.07 | 2968 | 130.61 | 3010 | 135.25 | 3051 | 139.85
21000 | 4062 | [18 empty] | 2464 | 82.54 | 2554 | 90.88 | 2642 | 99.38 | 2728 | 108.03 | 2771 | 112.5 | 2813 | 116.95 | 2855 | 121.48 | 2897 | 126.08 | 2938 | 130.63 | 2979 | 135.26 | 3020 | 139.98 | 3061 | 144.78 | 3101 | 149.53 | 3141 | 154.38 | 3180 | 159.16
22000 | 4255 | [18 empty] | 2494 | 86.48 | 2581 | 94.98 | 2666 | 103.61 | 2750 | 112.47 | 2791 | 116.91 | 2832 | 121.44 | 2873 | 126.07 | 2914 | 130.79 | 2954 | 135.46 | 2994 | 140.21 | 3033 | 144.89 | 3073 | 149.78 | 3112 | 154.61 | 3151 | 159.52 | 3190 | 164.51 | 3228 | 169.43 | 3266 | 174.43 | 3304 | 179.53
23000 | 4449 | [18 empty] | 2525 | 90.43 | 2610 | 99.2 | 2694 | 108.2 | 2775 | 117.16 | 2815 | 121.7 | 2855 | 126.33 | 2895 | 131.04 | 2934 | 135.71 | 2973 | 140.46 | 3012 | 145.3 | 3050 | 150.08 | 3088 | 154.94 | 3126 | 159.87 | 3164 | 164.86 | 3202 | 169.93 | 3239 | 174.92 | 3277 | 180.14
24000 | 4642 | [18 empty] | 2559 | 94.64 | 2642 | 103.68 | 2723 | 112.81 | 2802 | 122 | 2841 | 126.64 | 2880 | 131.36 | 2919 | 136.17 | 2957 | 140.92 | 2995 | 145.75 | 3033 | 150.66 | 3070 | 155.5 | 3107 | 160.43 | 3144 | 165.44 | 3181 | 170.53 | 3217 | 175.54 | 3254 | 180.77 | 3290 | 185.91
25000 | 4836 | [18 empty] | 2594 | 98.94 | 2675 | 108.2 | 2754 | 117.57 | 2831 | 126.98 | 2870 | 131.87 | 2908 | 136.7 | 2945 | 141.46 | 2982 | 146.29 | 3019 | 151.2 | 3056 | 156.19 | 3092 | 161.1 | 3129 | 166.24 | 3165 | 171.31 | 3200 | 176.29 | 3236 | 181.52 | 3271 | 186.66 | 3306 | 191.88
26000 | 5029 | [18 empty] | 2631 | 103.45 | 2710 | 112.93 | 2787 | 122.51 | 2862 | 132.14 | 2900 | 137.14 | 2937 | 142.07 | 2974 | 147.07 | 3010 | 152 | 3046 | 156.99 | 3082 | 162.06 | 3117 | 167.04 | 3153 | 172.25 | 3188 | 177.38 | 3222 | 182.41 | 3257 | 187.69 | 3291 | 192.86
27000 | 5222 | [18 empty] | 2670 | 108.23 | 2746 | 117.77 | 2821 | 127.54 | 2895 | 137.49 | 2932 | 142.59 | 2968 | 147.62 | 3004 | 152.72 | 3039 | 157.74 | 3074 | 162.81 | 3109 | 167.96 | 3144 | 173.18 | 3179 | 178.46 | 3213 | 183.65 | 3247 | 188.91 | 3281 | 194.24
28000 | 5416 | [18 empty] | 2710 | 113.17 | 2784 | 122.88 | 2857 | 132.81 | 2929 | 142.94 | 2965 | 148.13 | 3000 | 153.24 | 3035 | 158.42 | 3070 | 163.68 | 3105 | 169 | 3139 | 174.23 | 3173 | 179.53 | 3206 | 184.71 | 3240 | 190.14 | 3273 | 195.45 | 3306 | 200.84
29000 | 5609 | [18 empty] | 2752 | 118.43 | 2824 | 128.3 | 2895 | 138.38 | 2965 | 148.66 | 3000 | 153.92 | 3034 | 159.11 | 3068 | 164.36 | 3102 | 169.69 | 3136 | 175.09 | 3170 | 180.56 | 3203 | 185.93 | 3236 | 191.36 | 3269 | 196.86 | 3301 | 202.23
30000 | 5803 | [18 empty] | 2796 | 124.05 | 2865 | 133.91 | 2934 | 144.13 | 3002 | 154.54 | 3036 | 159.86 | 3070 | 165.27 | 3103 | 170.59 | 3136 | 175.98 | 3169 | 181.45 | 3202 | 186.98 | 3235 | 192.58 | 3267 | 198.07 | 3299 | 203.63
30500 | 5899 | [18 empty] | 2818 | 126.9 | 2886 | 136.82 | 2954 | 147.1 | 3021 | 157.56 | 3055 | 163 | 3088 | 168.35 | 3121 | 173.78 | 3154 | 179.28 | 3186 | 184.69 | 3219 | 190.34 | 3251 | 195.88 | 3283 | 201.49
31000 | 5996 | [36 empty] | 3236 | 193.69 | 3268 | 199.35 | 3299 | 204.88
31500 | 6093 | [36 empty] | 3253 | 197.03 | 3285 | 202.8
32000 | 6190 | [36 empty] | 3271 | 200.55 | 3302 | 206.25
32500 | 6286 | [36 empty] | 3289 | 204.07
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 3300HPB
3300HPB — Backward Curved High Pressure Fan
Outlet Area: 6.26 ft² Wheel Diameter: 33.00" Tip Speed (FPM): 8.64 x RPM
Max. RPM — Design 14: 1621 Design 17: 2199 Design 22: 2546 Design 26: 3009
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
8000 | 1278 | 715 | 3.2
9000 | 1438 | 739 | 3.61 | 970 | 7.4
10000 | 1597 | 766 | 4.05 | 984 | 8.05
11000 | 1757 | 798 | 4.58 | 1003 | 8.79 | 1187 | 13.56
12000 | 1917 | 832 | 5.17 | 1025 | 9.56 | 1200 | 14.52 | 1362 | 19.96
13000 | 2077 | 868 | 5.82 | 1051 | 10.42 | 1217 | 15.56 | 1372 | 21.18
14000 | 2236 | 906 | 6.56 | 1078 | 11.3 | 1238 | 16.71 | 1386 | 22.49 | 1527 | 28.75
15000 | 2396 | 946 | 7.38 | 1109 | 12.32 | 1262 | 17.94 | 1404 | 23.92 | 1539 | 30.33 | 1668 | 37.12
16000 | 2556 | 987 | 8.29 | 1141 | 13.39 | 1287 | 19.18 | 1425 | 25.46 | 1554 | 31.99 | 1678 | 38.93 | 1799 | 46.33
17000 | 2716 | 1029 | 9.29 | 1175 | 14.57 | 1315 | 20.54 | 1447 | 27 | 1573 | 33.82 | 1692 | 40.89 | 1808 | 48.41 | 1920 | 56.22
18000 | 2875 | 1072 | 10.39 | 1211 | 15.88 | 1344 | 21.96 | 1472 | 28.66 | 1593 | 35.67 | 1709 | 42.98 | 1821 | 50.66 | 1929 | 58.61 | 2035 | 66.96
19000 | 3035 | 1116 | 11.6 | 1249 | 17.31 | 1376 | 23.55 | 1499 | 30.43 | 1616 | 37.66 | 1728 | 45.16 | 1836 | 52.96 | 1941 | 61.13 | 2043 | 69.56
20000 | 3195 | 1160 | 12.89 | 1287 | 18.8 | 1409 | 25.24 | 1527 | 32.25 | 1641 | 39.75 | 1750 | 47.52 | 1855 | 55.54 | 1956 | 63.78 | 2055 | 72.41 | 2152 | 81.35 | 2246 | 90.47
21000 | 3355 | 1205 | 14.29 | 1327 | 20.45 | 1444 | 27.08 | 1557 | 34.21 | 1667 | 41.88 | 1773 | 49.9 | 1875 | 58.14 | 1973 | 66.55 | 2069 | 75.31 | 2163 | 84.41 | 2255 | 93.76 | 2345 | 103.36
22000 | 3514 | 1251 | 15.83 | 1367 | 22.18 | 1480 | 29.04 | 1589 | 36.33 | 1695 | 44.15 | 1798 | 52.39 | 1897 | 60.86 | 1993 | 69.55 | 2086 | 78.44 | 2177 | 87.65 | 2266 | 97.13 | 2354 | 106.94 | 2440 | 116.96 | 2482 | 122.01 | 2524 | 127.18
23000 | 3674 | 1297 | 17.48 | 1409 | 24.1 | 1517 | 31.12 | 1622 | 38.58 | 1724 | 46.51 | 1824 | 54.95 | 1921 | 63.71 | 2014 | 72.58 | 2105 | 81.73 | 2193 | 91.02 | 2280 | 100.7 | 2365 | 110.61 | 2449 | 120.82 | 2490 | 125.94 | 2531 | 131.17 | 2572 | 136.53 | 2612 | 141.85
24000 | 3834 | [18 empty] | 2212 | 94.69 | 2296 | 104.42 | 2379 | 114.51 | 2460 | 124.78 | 2500 | 129.99 | 2540 | 135.3 | 2580 | 140.73 | 2619 | 146.09 | 2658 | 151.57
25000 | 3994 | [18 empty] | 2232 | 98.4 | 2314 | 108.32 | 2395 | 118.57 | 2474 | 128.99 | 2513 | 134.3 | 2552 | 139.71 | 2590 | 145.05 | 2629 | 150.65 | 2667 | 156.19
26000 | 4153 | [18 empty] | 2253 | 102.17 | 2334 | 112.43 | 2412 | 122.69 | 2489 | 133.23 | 2528 | 138.76 | 2565 | 144.06 | 2603 | 149.65 | 2640 | 155.17 | 2677 | 160.78 | 2714 | 166.47 | 2751 | 172.27 | 2787 | 177.97 | 2824 | 183.97 | 2859 | 189.68 | 2895 | 195.7 | 2930 | 201.62 | 2965 | 207.65
27000 | 4313 | [18 empty] | 2276 | 106.14 | 2355 | 116.6 | 2432 | 127.18 | 2507 | 137.86 | 2544 | 143.28 | 2581 | 148.8 | 2618 | 154.43 | 2654 | 159.99 | 2690 | 165.67 | 2726 | 171.44 | 2762 | 177.3 | 2798 | 183.25 | 2833 | 189.09 | 2868 | 195.03 | 2903 | 201.06 | 2938 | 207.19 | 2972 | 213.21 | 3006 | 219.34
28000 | 4473 | [18 empty] | 2300 | 110.17 | 2377 | 120.83 | 2452 | 131.58 | 2526 | 142.56 | 2563 | 148.21 | 2599 | 153.79 | 2634 | 159.28 | 2670 | 165.06 | 2705 | 170.76 | 2740 | 176.56 | 2775 | 182.47 | 2810 | 188.49 | 2844 | 194.38 | 2879 | 200.57 | 2913 | 206.63 | 2947 | 212.78 | 2980 | 218.81
29000 | 4633 | [18 empty] | 2325 | 114.3 | 2401 | 125.3 | 2474 | 136.22 | 2547 | 147.52 | 2582 | 153.05 | 2618 | 158.86 | 2653 | 164.58 | 2687 | 170.21 | 2722 | 176.13 | 2756 | 181.96 | 2790 | 187.88 | 2824 | 193.91 | 2858 | 200.04 | 2891 | 206.06 | 2924 | 212.17 | 2957 | 218.35 | 2990 | 224.61
30000 | 4792 | [18 empty] | 2351 | 118.55 | 2425 | 129.7 | 2498 | 141.11 | 2568 | 152.38 | 2603 | 158.15 | 2638 | 164.01 | 2672 | 169.78 | 2706 | 175.64 | 2740 | 181.6 | 2774 | 187.65 | 2807 | 193.59 | 2840 | 199.63 | 2873 | 205.76 | 2906 | 211.99 | 2938 | 218.11 | 2970 | 224.31 | 3002 | 230.61
31000 | 4952 | [18 empty] | 2379 | 123.1 | 2451 | 134.39 | 2522 | 145.93 | 2591 | 157.51 | 2626 | 163.53 | 2660 | 169.45 | 2693 | 175.27 | 2727 | 181.37 | 2760 | 187.36 | 2792 | 193.23 | 2825 | 199.4 | 2857 | 205.45 | 2890 | 211.8 | 2922 | 218.04 | 2953 | 224.13 | 2985 | 230.55
32000 | 5112 | [18 empty] | 2407 | 127.65 | 2478 | 139.22 | 2547 | 150.88 | 2615 | 162.75 | 2649 | 168.83 | 2682 | 174.8 | 2715 | 180.86 | 2748 | 187.01 | 2780 | 193.03 | 2813 | 199.34 | 2845 | 205.54 | 2876 | 211.6 | 2908 | 217.96 | 2939 | 224.19 | 2970 | 230.51 | 3001 | 236.91
33000 | 5272 | [18 empty] | 2437 | 132.55 | 2506 | 144.22 | 2573 | 155.97 | 2640 | 168.12 | 2673 | 174.25 | 2706 | 180.46 | 2738 | 186.56 | 2770 | 192.74 | 2802 | 199.01 | 2834 | 205.36 | 2865 | 211.57 | 2896 | 217.86 | 2927 | 224.24 | 2958 | 230.69 | 2989 | 237.24
34000 | 5431 | [18 empty] | 2468 | 137.66 | 2534 | 149.24 | 2601 | 161.43 | 2666 | 173.65 | 2698 | 179.81 | 2730 | 186.06 | 2762 | 192.39 | 2794 | 198.82 | 2825 | 205.12 | 2856 | 211.49 | 2887 | 217.95 | 2918 | 224.48 | 2948 | 230.86 | 2978 | 237.32 | 3008 | 243.86
35000 | 5591 | [18 empty] | 2499 | 142.83 | 2564 | 154.65 | 2629 | 166.9 | 2693 | 179.36 | 2725 | 185.75 | 2756 | 192.02 | 2787 | 198.38 | 2818 | 204.83 | 2849 | 211.36 | 2879 | 217.75 | 2910 | 224.45 | 2940 | 231.01 | 2970 | 237.63 | 2999 | 244.09
35500 | 5671 | [36 empty] | 2891 | 220.97 | 2921 | 227.55 | 2951 | 234.23 | 2981 | 240.97
36000 | 5751 | [36 empty] | 2904 | 224.4 | 2933 | 230.87 | 2963 | 237.66 | 2992 | 244.29
36500 | 5831 | [36 empty] | 2916 | 227.59 | 2945 | 234.18 | 2975 | 241.09 | 3004 | 247.84
37000 | 5911 | [36 empty] | 2929 | 231 | 2958 | 237.7 | 2987 | 244.49
37500 | 5990 | [36 empty] | 2941 | 234.16 | 2970 | 240.98 | 2999 | 247.88
38000 | 6070 | [36 empty] | 2954 | 237.56 | 2983 | 244.49
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 3650HPB
3650HPB — Backward Curved High Pressure Fan
Outlet Area: 7.66 ft² Wheel Diameter: 36.50" Tip Speed (FPM): 9.56 x RPM
Max. RPM — Design 14: 1467 Design 17: 1987 Design 22: 2302 Design 26: 2720
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
10000 | 1305 | 650 | 4
11000 | 1436 | 668 | 4.41 | 877 | 9.05
12000 | 1567 | 688 | 4.85 | 887 | 9.7
13000 | 1697 | 710 | 5.34 | 900 | 10.41 | 1069 | 16.13
14000 | 1828 | 734 | 5.89 | 915 | 11.15 | 1077 | 17.06
15000 | 1958 | 760 | 6.51 | 933 | 11.98 | 1089 | 18.1 | 1234 | 24.83
16000 | 2089 | 787 | 7.18 | 952 | 12.83 | 1102 | 19.16 | 1241 | 26.02 | 1374 | 33.52
17000 | 2219 | 815 | 7.91 | 972 | 13.71 | 1117 | 20.28 | 1252 | 27.36 | 1380 | 35
18000 | 2350 | 845 | 8.74 | 994 | 14.68 | 1134 | 21.48 | 1264 | 28.72 | 1388 | 36.54 | 1506 | 44.79
19000 | 2480 | 875 | 9.61 | 1018 | 15.76 | 1153 | 22.76 | 1279 | 30.24 | 1398 | 38.14 | 1513 | 46.62 | 1623 | 55.47
20000 | 2611 | 905 | 10.54 | 1042 | 16.87 | 1172 | 24.02 | 1295 | 31.79 | 1411 | 39.92 | 1521 | 48.44 | 1629 | 57.55
21000 | 2742 | 937 | 11.59 | 1068 | 18.1 | 1193 | 25.4 | 1312 | 33.37 | 1425 | 41.75 | 1532 | 50.43 | 1636 | 59.63 | 1737 | 69.24
22000 | 2872 | 969 | 12.71 | 1095 | 19.43 | 1215 | 26.86 | 1331 | 35.08 | 1440 | 43.61 | 1545 | 52.56 | 1646 | 61.91 | 1744 | 71.67 | 1840 | 81.89
23000 | 3003 | 1001 | 13.88 | 1122 | 20.8 | 1238 | 28.4 | 1350 | 36.76 | 1457 | 45.61 | 1559 | 54.74 | 1657 | 64.21 | 1753 | 74.22 | 1846 | 84.53 | 1936 | 95.11
24000 | 3133 | 1034 | 15.17 | 1150 | 22.27 | 1262 | 30.05 | 1371 | 38.61 | 1475 | 47.66 | 1574 | 56.98 | 1670 | 66.68 | 1763 | 76.76 | 1854 | 87.31 | 1942 | 98.05 | 2028 | 109.16
25000 | 3264 | 1067 | 16.53 | 1179 | 23.85 | 1288 | 31.88 | 1392 | 40.46 | 1494 | 49.78 | 1591 | 59.38 | 1685 | 69.34 | 1775 | 79.49 | 1863 | 90.08 | 1950 | 101.18 | 2034 | 112.42 | 2117 | 124.15
26000 | 3394 | [18 empty] | 1959 | 104.32 | 2041 | 115.72 | 2122 | 127.54 | 2201 | 139.63
27000 | 3525 | [18 empty] | 1969 | 107.47 | 2050 | 119.21 | 2129 | 131.16 | 2206 | 143.3 | 2245 | 149.7 | 2282 | 155.86
28000 | 3655 | [18 empty] | 1981 | 110.88 | 2060 | 122.72 | 2137 | 134.81 | 2213 | 147.24 | 2250 | 153.45 | 2288 | 160.02 | 2324 | 166.32 | 2361 | 172.98
29000 | 3786 | [18 empty] | 1994 | 114.38 | 2071 | 126.31 | 2147 | 138.67 | 2221 | 151.21 | 2258 | 157.67 | 2294 | 164.05 | 2330 | 170.57 | 2366 | 177.22 | 2401 | 183.78 | 2436 | 190.49
30000 | 3916 | [18 empty] | 2009 | 118.16 | 2084 | 130.19 | 2158 | 142.61 | 2230 | 155.22 | 2266 | 161.73 | 2302 | 168.35 | 2337 | 174.88 | 2372 | 181.54 | 2407 | 188.32 | 2442 | 195.24 | 2476 | 202.06 | 2510 | 209.02 | 2543 | 215.87
31000 | 4047 | [18 empty] | 2024 | 121.88 | 2098 | 134.19 | 2170 | 146.67 | 2241 | 159.5 | 2276 | 166.02 | 2311 | 172.69 | 2346 | 179.48 | 2380 | 186.15 | 2414 | 192.94 | 2448 | 199.84 | 2482 | 206.88 | 2515 | 213.8 | 2548 | 220.84 | 2581 | 228.02 | 2613 | 235.07
32000 | 4178 | [18 empty] | 2040 | 125.72 | 2113 | 138.32 | 2184 | 151.06 | 2253 | 163.91 | 2288 | 170.66 | 2322 | 177.32 | 2355 | 183.89 | 2389 | 190.81 | 2422 | 197.61 | 2456 | 204.77 | 2489 | 211.79 | 2522 | 218.94 | 2554 | 225.94 | 2586 | 233.07 | 2618 | 240.31 | 2650 | 247.69 | 2682 | 255.21
33000 | 4308 | [18 empty] | 2057 | 129.68 | 2128 | 142.37 | 2198 | 155.38 | 2266 | 168.47 | 2300 | 175.21 | 2333 | 181.86 | 2366 | 188.63 | 2399 | 195.54 | 2432 | 202.59 | 2465 | 209.75 | 2497 | 216.78 | 2529 | 223.9 | 2561 | 231.14 | 2593 | 238.49 | 2624 | 245.69 | 2656 | 253.28 | 2687 | 260.72 | 2718 | 268.27
34000 | 4439 | [18 empty] | 2075 | 133.77 | 2145 | 146.77 | 2213 | 159.84 | 2280 | 173.17 | 2313 | 179.91 | 2346 | 186.78 | 2379 | 193.78 | 2411 | 200.66 | 2443 | 207.67 | 2475 | 214.81 | 2506 | 221.82 | 2538 | 229.2 | 2569 | 236.42 | 2600 | 243.74 | 2631 | 251.17 | 2662 | 258.7 | 2693 | 266.36
35000 | 4569 | [18 empty] | 2093 | 137.82 | 2162 | 151.1 | 2229 | 164.44 | 2295 | 178.03 | 2328 | 185.01 | 2360 | 191.87 | 2392 | 198.85 | 2423 | 205.7 | 2455 | 212.93 | 2486 | 220.02 | 2517 | 227.23 | 2548 | 234.58 | 2579 | 242.05 | 2609 | 249.35 | 2640 | 257.03 | 2670 | 264.52 | 2700 | 272.12
36000 | 4700 | [18 empty] | 2112 | 142.04 | 2180 | 155.58 | 2246 | 169.2 | 2311 | 183.05 | 2343 | 190.03 | 2374 | 196.88 | 2406 | 204.09 | 2437 | 211.17 | 2468 | 218.36 | 2498 | 225.4 | 2529 | 232.84 | 2559 | 240.12 | 2589 | 247.52 | 2619 | 255.04 | 2649 | 262.68 | 2679 | 270.44 | 2708 | 277.98
37000 | 4830 | [18 empty] | 2132 | 146.44 | 2198 | 160.03 | 2263 | 173.9 | 2327 | 188 | 2359 | 195.22 | 2390 | 202.31 | 2421 | 209.51 | 2451 | 216.55 | 2482 | 223.98 | 2512 | 231.25 | 2542 | 238.63 | 2571 | 245.85 | 2601 | 253.46 | 2630 | 260.91 | 2660 | 268.77 | 2689 | 276.44 | 2717 | 283.93
38000 | 4961 | [18 empty] | 2152 | 150.84 | 2217 | 164.66 | 2281 | 178.77 | 2344 | 193.12 | 2375 | 200.34 | 2406 | 207.67 | 2436 | 214.85 | 2466 | 222.13 | 2496 | 229.51 | 2526 | 237.02 | 2555 | 244.34 | 2584 | 251.78 | 2614 | 259.62 | 2642 | 266.98 | 2671 | 274.75 | 2700 | 282.64
39000 | 5091 | [36 empty] | 2541 | 242.98 | 2570 | 250.54 | 2598 | 257.92 | 2627 | 265.69 | 2655 | 273.27 | 2684 | 281.27 | 2712 | 289.06
40000 | 5222 | [36 empty] | 2556 | 248.87 | 2585 | 256.67 | 2613 | 264.27 | 2641 | 271.97 | 2669 | 279.78 | 2697 | 287.69
41000 | 5352 | [36 empty] | 2572 | 254.96 | 2601 | 263 | 2628 | 270.54 | 2656 | 278.48 | 2684 | 286.52 | 2711 | 294.34
42000 | 5483 | [36 empty] | 2589 | 261.28 | 2617 | 269.26 | 2644 | 277.04 | 2672 | 285.22 | 2699 | 293.18
43000 | 5614 | [36 empty] | 2607 | 267.82 | 2634 | 275.75 | 2661 | 283.77 | 2688 | 291.88 | 2715 | 300.08
44000 | 5744 | [36 empty] | 2624 | 274.01 | 2651 | 282.16 | 2678 | 290.42 | 2705 | 298.78
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 4025HPB
4025HPB — Backward Curved High Pressure Fan
Outlet Area: 9.31 ft² Wheel Diameter: 40.25" Tip Speed (FPM): 10.54 x RPM
Max. RPM — Design 14: 1329 Design 17: 1802 Design 22: 2088 Design 26: 2467
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
15000 | 1611 | 630 | 6.08 | 808 | 12.07
16000 | 1719 | 647 | 6.59 | 818 | 12.79 | 971 | 19.83
17000 | 1826 | 666 | 7.17 | 830 | 13.57 | 977 | 20.75
18000 | 1933 | 685 | 7.78 | 843 | 14.38 | 985 | 21.74 | 1118 | 29.92
19000 | 2041 | 705 | 8.44 | 856 | 15.17 | 995 | 22.83 | 1123 | 31.11
20000 | 2148 | 725 | 9.12 | 871 | 16.06 | 1005 | 23.88 | 1130 | 32.4 | 1248 | 41.53
21000 | 2256 | 747 | 9.91 | 887 | 17 | 1017 | 25.05 | 1138 | 33.7 | 1253 | 43.04
22000 | 2363 | 768 | 10.69 | 903 | 17.95 | 1030 | 26.27 | 1148 | 35.14 | 1259 | 44.57 | 1366 | 54.64
23000 | 2470 | 791 | 11.59 | 921 | 19.03 | 1044 | 27.53 | 1159 | 36.64 | 1267 | 46.22 | 1371 | 56.45
24000 | 2578 | 814 | 12.54 | 939 | 20.14 | 1058 | 28.79 | 1170 | 38.11 | 1276 | 47.93 | 1377 | 58.28 | 1475 | 69.22
25000 | 2685 | 837 | 13.53 | 958 | 21.34 | 1073 | 30.11 | 1183 | 39.74 | 1286 | 49.72 | 1385 | 60.28 | 1481 | 71.45 | 1573 | 82.96
26000 | 2793 | 860 | 14.57 | 978 | 22.64 | 1089 | 31.53 | 1196 | 41.34 | 1297 | 51.58 | 1394 | 62.35 | 1487 | 73.58 | 1578 | 85.41
27000 | 2900 | 884 | 15.7 | 998 | 23.97 | 1106 | 33.04 | 1210 | 43.02 | 1309 | 53.53 | 1403 | 64.37 | 1494 | 75.76 | 1583 | 87.77 | 1669 | 100.13
28000 | 3008 | 909 | 16.95 | 1018 | 25.33 | 1123 | 34.57 | 1225 | 44.79 | 1322 | 55.56 | 1414 | 66.62 | 1503 | 78.17 | 1590 | 90.35 | 1674 | 102.84 | 1756 | 115.79
29000 | 3115 | 933 | 18.2 | 1039 | 26.81 | 1141 | 36.22 | 1240 | 46.56 | 1335 | 57.56 | 1426 | 68.98 | 1513 | 80.69 | 1597 | 92.82 | 1680 | 105.63 | 1760 | 118.65 | 1839 | 132.3
30000 | 3222 | 958 | 19.56 | 1061 | 28.4 | 1160 | 38 | 1256 | 48.45 | 1349 | 59.67 | 1438 | 71.3 | 1523 | 83.17 | 1606 | 95.57 | 1687 | 108.5 | 1766 | 121.82 | 1843 | 135.48
31000 | 3330 | [18 empty] | 1772 | 124.87 | 1848 | 138.79 | 1922 | 153.02
32000 | 3437 | [18 empty] | 1779 | 128.01 | 1853 | 141.98 | 1926 | 156.42 | 1997 | 171.12 | 2032 | 178.64
33000 | 3545 | [18 empty] | 1787 | 131.26 | 1860 | 145.5 | 1931 | 159.96 | 2002 | 175.1 | 2036 | 182.55 | 2070 | 190.19
34000 | 3652 | [18 empty] | 1796 | 134.67 | 1867 | 148.89 | 1938 | 163.86 | 2007 | 178.97 | 2041 | 186.65 | 2074 | 194.22 | 2108 | 202.25 | 2141 | 210.18
35000 | 3759 | [18 empty] | 1806 | 138.25 | 1876 | 152.68 | 1945 | 167.63 | 2012 | 182.71 | 2046 | 190.62 | 2079 | 198.42 | 2112 | 206.38 | 2144 | 214.22 | 2177 | 222.54 | 2208 | 230.42
36000 | 3867 | [18 empty] | 1816 | 141.78 | 1885 | 156.41 | 1953 | 171.54 | 2019 | 186.85 | 2052 | 194.74 | 2084 | 202.49 | 2117 | 210.68 | 2149 | 218.74 | 2181 | 226.97 | 2212 | 235.05 | 2243 | 243.29 | 2274 | 251.71
37000 | 3974 | [18 empty] | 1827 | 145.48 | 1895 | 160.34 | 1961 | 175.38 | 2027 | 191.13 | 2059 | 198.99 | 2091 | 207 | 2123 | 215.15 | 2154 | 223.14 | 2185 | 231.28 | 2217 | 239.9 | 2247 | 248.02 | 2278 | 256.64 | 2308 | 265.1 | 2338 | 273.72
38000 | 4082 | [18 empty] | 1839 | 149.37 | 1906 | 164.46 | 1971 | 179.69 | 2035 | 195.33 | 2067 | 203.41 | 2098 | 211.36 | 2129 | 219.46 | 2160 | 227.7 | 2191 | 236.09 | 2222 | 244.62 | 2252 | 252.97 | 2282 | 261.47 | 2312 | 270.13 | 2342 | 278.95 | 2371 | 287.57 | 2400 | 296.37
39000 | 4189 | [18 empty] | 1851 | 153.22 | 1917 | 168.52 | 1981 | 183.95 | 2044 | 199.74 | 2075 | 207.74 | 2106 | 215.91 | 2137 | 224.24 | 2167 | 232.43 | 2197 | 240.74 | 2227 | 249.19 | 2257 | 257.77 | 2287 | 266.51 | 2317 | 275.39 | 2346 | 284.07 | 2375 | 292.9 | 2404 | 301.89 | 2432 | 310.65 | 2460 | 319.58
40000 | 4296 | [18 empty] | 1864 | 157.26 | 1929 | 172.8 | 1992 | 188.43 | 2054 | 204.39 | 2084 | 212.31 | 2115 | 220.69 | 2145 | 228.93 | 2175 | 237.33 | 2204 | 245.57 | 2234 | 254.27 | 2263 | 262.77 | 2293 | 271.75 | 2322 | 280.51 | 2351 | 289.42 | 2379 | 298.1 | 2408 | 307.3 | 2436 | 316.27 | 2464 | 325.39
41000 | 4404 | [18 empty] | 1877 | 161.25 | 1941 | 177.03 | 2003 | 192.85 | 2064 | 208.98 | 2094 | 217.12 | 2124 | 225.42 | 2154 | 233.87 | 2183 | 242.16 | 2212 | 250.6 | 2241 | 259.2 | 2270 | 267.95 | 2299 | 276.83 | 2328 | 285.85 | 2356 | 294.62 | 2384 | 303.53 | 2412 | 312.57 | 2440 | 321.75
42000 | 4511 | [18 empty] | 1890 | 165.2 | 1953 | 181.19 | 2015 | 197.5 | 2075 | 213.81 | 2105 | 222.18 | 2134 | 230.39 | 2163 | 238.74 | 2192 | 247.24 | 2221 | 255.9 | 2250 | 264.72 | 2278 | 273.34 | 2306 | 282.1 | 2334 | 291.01 | 2362 | 300.04 | 2390 | 309.19 | 2418 | 318.47 | 2445 | 327.5
43000 | 4619 | [18 empty] | 1904 | 169.39 | 1966 | 185.59 | 2027 | 202.1 | 2086 | 218.57 | 2116 | 227.19 | 2145 | 235.63 | 2173 | 243.88 | 2202 | 252.6 | 2230 | 261.14 | 2258 | 269.81 | 2286 | 278.64 | 2314 | 287.62 | 2342 | 296.76 | 2369 | 305.66 | 2397 | 315.08 | 2424 | 324.22 | 2451 | 333.48
45000 | 4834 | [36 empty] | 2278 | 281.24 | 2305 | 290.14 | 2332 | 299.18 | 2359 | 308.36 | 2385 | 317.3 | 2412 | 326.78 | 2438 | 335.99 | 2464 | 345.35
47000 | 5048 | [36 empty] | 2299 | 292.76 | 2326 | 302.12 | 2352 | 311.23 | 2378 | 320.47 | 2404 | 329.84 | 2429 | 338.93 | 2455 | 348.57
49000 | 5263 | [36 empty] | 2322 | 304.77 | 2348 | 314.22 | 2374 | 323.8 | 2399 | 333.09 | 2424 | 342.5 | 2449 | 352.04
51000 | 5478 | [36 empty] | 2347 | 317.32 | 2372 | 326.85 | 2397 | 336.5 | 2422 | 346.26 | 2446 | 355.72
53000 | 5693 | [36 empty] | 2373 | 330.03 | 2398 | 340.06 | 2422 | 349.77 | 2446 | 359.59
55000 | 5908 | [36 empty] | 2400 | 343.01 | 2424 | 353.06 | 2448 | 363.25
57000 | 6122 | [36 empty] | 2429 | 356.75 | 2453 | 367.27
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 4450HPB
4450HPB — Backward Curved High Pressure Fan
Outlet Area: 11.39 ft² Wheel Diameter: 44.50" Tip Speed (FPM): 11.65 x RPM
Max. RPM — Design 14: 1202 Design 17: 1631 Design 22: 1888 Design 26: 2231
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
17000 | 1493 | 555 | 6.84 | 722 | 13.83
18500 | 1624 | 572 | 7.52 | 732 | 14.87 | 874 | 23.23
20000 | 1756 | 591 | 8.29 | 744 | 15.99 | 880 | 24.63
21500 | 1888 | 612 | 9.18 | 757 | 17.13 | 888 | 26.09 | 1009 | 35.91
23000 | 2019 | 634 | 10.15 | 772 | 18.36 | 898 | 27.63 | 1015 | 37.77
24500 | 2151 | 657 | 11.21 | 789 | 19.72 | 910 | 29.31 | 1022 | 39.62 | 1129 | 50.85
26000 | 2283 | 681 | 12.38 | 806 | 21.08 | 923 | 31.02 | 1032 | 41.7 | 1135 | 53.15
27500 | 2414 | 705 | 13.61 | 825 | 22.61 | 938 | 32.89 | 1043 | 43.83 | 1142 | 55.44 | 1238 | 67.93
29000 | 2546 | 730 | 14.97 | 845 | 24.26 | 954 | 34.82 | 1056 | 46.16 | 1152 | 58.04 | 1244 | 70.64 | 1333 | 83.91
30500 | 2678 | 756 | 16.47 | 866 | 26.04 | 970 | 36.74 | 1069 | 48.42 | 1163 | 60.71 | 1252 | 73.5 | 1339 | 87.15 | 1423 | 101.36
32000 | 2809 | 782 | 18.07 | 887 | 27.88 | 988 | 38.89 | 1084 | 50.89 | 1175 | 63.47 | 1262 | 76.6 | 1346 | 90.41 | 1428 | 104.9 | 1507 | 119.86
33500 | 2941 | 809 | 19.82 | 910 | 29.96 | 1007 | 41.19 | 1100 | 53.47 | 1189 | 66.49 | 1273 | 79.8 | 1355 | 93.89 | 1434 | 108.49 | 1511 | 123.64
35000 | 3073 | 836 | 21.68 | 933 | 32.12 | 1026 | 43.52 | 1116 | 56.03 | 1203 | 69.44 | 1286 | 83.3 | 1365 | 97.47 | 1442 | 112.33 | 1517 | 127.74
36500 | 3205 | 863 | 23.64 | 957 | 34.46 | 1047 | 46.17 | 1134 | 58.89 | 1218 | 72.5 | 1299 | 86.73 | 1376 | 101.18 | 1451 | 116.24 | 1525 | 132.15 | 1596 | 148.21 | 1666 | 164.93
38000 | 3336 | 890 | 25.71 | 981 | 36.87 | 1068 | 48.88 | 1152 | 61.78 | 1234 | 75.72 | 1313 | 90.28 | 1389 | 105.25 | 1462 | 120.54 | 1533 | 136.35 | 1603 | 152.89 | 1672 | 170.03 | 1738 | 187.17
39500 | 3468 | 918 | 27.98 | 1006 | 39.51 | 1090 | 51.79 | 1172 | 65.03 | 1251 | 79.1 | 1328 | 93.98 | 1402 | 109.25 | 1474 | 125 | 1543 | 140.96 | 1611 | 157.62 | 1678 | 174.92 | 1744 | 192.75 | 1808 | 210.82 | 1839 | 219.85
41000 | 3600 | [18 empty] | 1621 | 162.79 | 1686 | 180.19 | 1750 | 198.12 | 1813 | 216.52 | 1844 | 225.87 | 1874 | 235.06 | 1905 | 244.86
42500 | 3731 | [18 empty] | 1631 | 167.85 | 1695 | 185.58 | 1757 | 203.58 | 1819 | 222.37 | 1849 | 231.69 | 1879 | 241.21 | 1909 | 250.93 | 1939 | 260.88 | 1968 | 270.64
44000 | 3863 | [18 empty] | 1643 | 173.43 | 1705 | 191.2 | 1766 | 209.5 | 1826 | 228.32 | 1856 | 238.02 | 1885 | 247.51 | 1915 | 257.59 | 1944 | 267.46 | 1972 | 277.12
45500 | 3995 | [18 empty] | 1655 | 178.92 | 1716 | 197.03 | 1776 | 215.65 | 1835 | 234.77 | 1864 | 244.46 | 1892 | 253.94 | 1921 | 263.99 | 1950 | 274.23 | 1978 | 284.23
47000 | 4126 | [18 empty] | 1668 | 184.62 | 1728 | 203.11 | 1787 | 222.06 | 1844 | 241.07 | 1873 | 251.09 | 1901 | 260.91 | 1929 | 270.95 | 1957 | 281.15 | 1984 | 291.08 | 2012 | 301.62 | 2039 | 311.9 | 2066 | 322.36 | 2093 | 332.99 | 2120 | 343.83 | 2146 | 354.37 | 2172 | 365.11 | 2198 | 376.04
48500 | 4258 | [18 empty] | 1682 | 190.57 | 1741 | 209.45 | 1798 | 228.36 | 1855 | 248.05 | 1883 | 257.99 | 1910 | 267.73 | 1938 | 278.08 | 1965 | 288.2 | 1992 | 298.53 | 2019 | 309.01 | 2045 | 319.19 | 2072 | 330 | 2098 | 340.51 | 2125 | 351.68 | 2151 | 362.54 | 2176 | 373.07 | 2202 | 384.29 | 2228 | 395.72
50000 | 4390 | [18 empty] | 1697 | 196.77 | 1754 | 215.68 | 1811 | 235.31 | 1866 | 254.9 | 1893 | 264.78 | 1920 | 274.83 | 1947 | 285.08 | 1974 | 295.52 | 2000 | 305.71 | 2027 | 316.56 | 2053 | 327.12 | 2079 | 337.84 | 2105 | 348.72 | 2131 | 359.76 | 2156 | 370.45 | 2182 | 381.84 | 2207 | 392.86
51500 | 4522 | [18 empty] | 1712 | 202.91 | 1768 | 222.18 | 1824 | 242.16 | 1878 | 262.06 | 1905 | 272.28 | 1931 | 282.24 | 1958 | 292.83 | 1984 | 303.16 | 2010 | 313.67 | 2036 | 324.37 | 2061 | 334.77 | 2087 | 345.86 | 2112 | 356.63 | 2137 | 367.53 | 2163 | 379.12 | 2188 | 390.33 | 2212 | 401.17
53000 | 4653 | [18 empty] | 1727 | 208.99 | 1783 | 228.97 | 1837 | 248.9 | 1891 | 269.52 | 1917 | 279.66 | 1943 | 289.97 | 1969 | 300.46 | 1995 | 311.13 | 2020 | 321.5 | 2046 | 332.53 | 2071 | 343.26 | 2096 | 354.17 | 2121 | 365.27 | 2145 | 376.02 | 2170 | 387.47 | 2194 | 398.53 | 2219 | 410.28
54500 | 4785 | [18 empty] | 1743 | 215.4 | 1798 | 235.69 | 1852 | 256.36 | 1904 | 276.88 | 1930 | 287.38 | 1956 | 298.05 | 1981 | 308.43 | 2007 | 319.45 | 2032 | 330.16 | 2056 | 340.56 | 2081 | 351.61 | 2106 | 362.85 | 2130 | 373.75 | 2154 | 384.81 | 2178 | 396.05 | 2202 | 407.48 | 2226 | 419.06
56000 | 4917 | [18 empty] | 1760 | 222.17 | 1814 | 242.77 | 1866 | 263.32 | 1918 | 284.56 | 1944 | 295.43 | 1969 | 306.01 | 1994 | 316.75 | 2019 | 327.65 | 2043 | 338.22 | 2068 | 349.45 | 2092 | 360.34 | 2116 | 371.4 | 2140 | 382.62 | 2164 | 394.01 | 2188 | 405.58 | 2211 | 416.76
57500 | 5048 | [18 empty] | 1777 | 228.94 | 1830 | 249.81 | 1882 | 271.06 | 1933 | 292.59 | 1958 | 303.39 | 1983 | 314.34 | 2007 | 324.95 | 2032 | 336.22 | 2056 | 347.14 | 2080 | 358.22 | 2104 | 369.46 | 2128 | 380.86 | 2151 | 391.89 | 2175 | 403.62 | 2198 | 414.97 | 2221 | 426.47
59000 | 5180 | [18 empty] | 1795 | 236.13 | 1847 | 257.27 | 1897 | 278.33 | 1948 | 300.55 | 1972 | 311.23 | 1997 | 322.54 | 2021 | 333.54 | 2045 | 344.67 | 2069 | 355.95 | 2093 | 367.39 | 2116 | 378.45 | 2140 | 390.21 | 2163 | 401.58 | 2186 | 413.1 | 2209 | 424.77 | 2231 | 436.03
60500 | 5312 | [36 empty] | 2106 | 376.45 | 2129 | 387.86 | 2152 | 399.43 | 2175 | 411.14 | 2198 | 423.02 | 2220 | 434.46
62000 | 5443 | [36 empty] | 2120 | 385.91 | 2143 | 397.7 | 2165 | 409.07 | 2188 | 421.15 | 2210 | 432.8
63500 | 5575 | [36 empty] | 2134 | 395.26 | 2156 | 406.86 | 2179 | 419.17 | 2201 | 431.03 | 2223 | 443.04
65000 | 5707 | [36 empty] | 2149 | 405.09 | 2171 | 417.04 | 2193 | 429.14 | 2215 | 441.38
66500 | 5838 | [36 empty] | 2164 | 414.84 | 2186 | 427.15 | 2207 | 439.01 | 2229 | 451.61
68000 | 5970 | [36 empty] | 2179 | 424.54 | 2201 | 437.19 | 2222 | 449.39
69500 | 6102 | [36 empty] | 2195 | 434.78 | 2216 | 447.18
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 4900HPB
4900HPB — Backward Curved High Pressure Fan
Outlet Area: 13.8 ft² Wheel Diameter: 49.00" Tip Speed (FPM): 12.83 x RPM
Max. RPM — Design 14: 1092 Design 17: 1481 Design 22: 1780 Design 26: 2027
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
20000 | 1449 | 499 | 8.03 | 654 | 16.42
22000 | 1594 | 516 | 8.93 | 662 | 17.69
24000 | 1739 | 535 | 9.96 | 674 | 19.19 | 798 | 29.59
26000 | 1884 | 555 | 11.08 | 687 | 20.72 | 806 | 31.55 | 916 | 43.43
28000 | 2029 | 577 | 12.38 | 702 | 22.36 | 816 | 33.61 | 922 | 45.92
30000 | 2174 | 600 | 13.8 | 719 | 24.17 | 828 | 35.83 | 930 | 48.52 | 1026 | 62.08
32000 | 2319 | 624 | 15.38 | 736 | 25.99 | 842 | 38.24 | 939 | 51.11 | 1032 | 65.11 | 1121 | 79.99
34000 | 2464 | 648 | 17.05 | 756 | 28.15 | 857 | 40.71 | 951 | 54.09 | 1040 | 68.29 | 1126 | 83.51
36000 | 2609 | 674 | 18.99 | 776 | 30.38 | 873 | 43.28 | 964 | 57.16 | 1051 | 71.91 | 1133 | 87.25 | 1213 | 103.55
38000 | 2754 | 700 | 21.06 | 797 | 32.8 | 890 | 46 | 979 | 60.5 | 1062 | 75.43 | 1142 | 91.21 | 1219 | 107.75 | 1295 | 125.37
40000 | 2899 | 726 | 23.26 | 819 | 35.42 | 908 | 48.88 | 994 | 63.77 | 1075 | 79.27 | 1153 | 95.52 | 1228 | 112.48 | 1300 | 129.96 | 1371 | 148.37
42000 | 3043 | 753 | 25.7 | 842 | 38.27 | 928 | 52.15 | 1010 | 67.19 | 1089 | 83.23 | 1165 | 99.97 | 1237 | 117.02 | 1308 | 135.16 | 1377 | 153.92
44000 | 3188 | 780 | 28.29 | 866 | 41.37 | 948 | 55.49 | 1028 | 71.01 | 1104 | 87.34 | 1178 | 104.56 | 1248 | 121.99 | 1317 | 140.41 | 1384 | 159.52 | 1449 | 179.06 | 1513 | 199.39
46000 | 3333 | 808 | 31.15 | 890 | 44.58 | 969 | 59.1 | 1046 | 74.86 | 1120 | 91.62 | 1192 | 109.32 | 1261 | 127.43 | 1327 | 145.83 | 1392 | 165.14 | 1456 | 185.33 | 1518 | 205.82 | 1579 | 227.02
48000 | 3478 | 835 | 34.06 | 915 | 48.1 | 991 | 62.99 | 1065 | 78.98 | 1137 | 96.14 | 1207 | 114.25 | 1274 | 132.76 | 1339 | 151.78 | 1402 | 171.3 | 1464 | 191.64 | 1524 | 212.33 | 1584 | 234.03 | 1642 | 255.92 | 1671 | 267.29
50000 | 3623 | 863 | 37.27 | 940 | 51.78 | 1013 | 67 | 1085 | 83.41 | 1155 | 100.93 | 1222 | 119.12 | 1288 | 138.28 | 1352 | 157.96 | 1413 | 177.68 | 1473 | 198.12 | 1532 | 219.32 | 1590 | 241.16 | 1647 | 263.5 | 1675 | 274.81 | 1703 | 286.4 | 1730 | 297.75 | 1758 | 309.89
52000 | 3768 | [18 empty] | 1484 | 205.26 | 1542 | 226.92 | 1598 | 248.82 | 1653 | 271.22 | 1681 | 283.01 | 1708 | 294.54 | 1735 | 306.31 | 1762 | 318.34 | 1788 | 330.09
54000 | 3913 | [18 empty] | 1496 | 212.67 | 1552 | 234.37 | 1607 | 256.66 | 1661 | 279.54 | 1688 | 291.35 | 1714 | 302.84 | 1741 | 315.09 | 1767 | 327.03 | 1793 | 339.2
56000 | 4058 | [18 empty] | 1509 | 220.37 | 1564 | 242.57 | 1617 | 264.81 | 1670 | 288.05 | 1696 | 299.81 | 1722 | 311.82 | 1748 | 324.04 | 1773 | 335.91 | 1799 | 348.56
58000 | 4203 | [18 empty] | 1522 | 227.93 | 1576 | 250.62 | 1628 | 273.28 | 1680 | 296.91 | 1706 | 309.09 | 1731 | 320.99 | 1756 | 333.12 | 1781 | 345.51 | 1806 | 358.1 | 1830 | 370.28 | 1855 | 383.27 | 1879 | 395.87 | 1903 | 408.66 | 1927 | 421.68 | 1951 | 434.91 | 1975 | 448.4 | 1998 | 461.42 | 2021 | 474.69
60000 | 4348 | [18 empty] | 1536 | 235.79 | 1589 | 258.99 | 1641 | 282.62 | 1691 | 306.12 | 1716 | 318.21 | 1741 | 330.54 | 1765 | 342.53 | 1790 | 355.34 | 1814 | 367.81 | 1838 | 380.5 | 1862 | 393.39 | 1886 | 406.48 | 1909 | 419.1 | 1933 | 432.59 | 1956 | 445.61 | 1980 | 459.52 | 2003 | 472.97 | 2025 | 485.92
62000 | 4493 | [18 empty] | 1551 | 244 | 1603 | 267.71 | 1653 | 291.28 | 1703 | 315.71 | 1727 | 327.7 | 1752 | 340.48 | 1776 | 352.92 | 1800 | 365.58 | 1823 | 377.86 | 1847 | 390.98 | 1870 | 403.7 | 1893 | 416.64 | 1917 | 430.44 | 1940 | 443.77 | 1962 | 456.58 | 1985 | 470.28 | 2008 | 484.17
64000 | 4638 | [18 empty] | 1566 | 252.13 | 1617 | 276.29 | 1667 | 300.84 | 1716 | 325.7 | 1739 | 337.58 | 1763 | 350.25 | 1787 | 363.14 | 1810 | 375.64 | 1833 | 388.34 | 1857 | 401.91 | 1879 | 414.39 | 1902 | 427.76 | 1925 | 441.36 | 1947 | 454.49 | 1970 | 468.51 | 1992 | 482.01 | 2014 | 495.67
66000 | 4783 | [18 empty] | 1582 | 260.68 | 1632 | 285.27 | 1681 | 310.26 | 1729 | 335.54 | 1752 | 347.89 | 1776 | 361.04 | 1799 | 373.79 | 1822 | 386.75 | 1845 | 399.92 | 1867 | 412.63 | 1890 | 426.22 | 1912 | 439.36 | 1934 | 452.69 | 1956 | 466.24 | 1978 | 480.01 | 2000 | 493.99 | 2021 | 507.43
68000 | 4928 | [18 empty] | 1599 | 269.71 | 1648 | 294.71 | 1696 | 320.11 | 1743 | 345.8 | 1766 | 358.64 | 1789 | 371.67 | 1812 | 384.9 | 1834 | 397.69 | 1856 | 410.66 | 1879 | 424.5 | 1901 | 437.88 | 1923 | 451.45 | 1944 | 464.52 | 1966 | 478.5 | 1987 | 491.97 | 2009 | 506.38
70000 | 5072 | [18 empty] | 1616 | 278.76 | 1664 | 304.11 | 1711 | 329.87 | 1757 | 355.9 | 1780 | 369.23 | 1803 | 382.76 | 1825 | 395.84 | 1847 | 409.11 | 1869 | 422.55 | 1891 | 436.2 | 1912 | 449.34 | 1934 | 463.36 | 1955 | 476.88 | 1976 | 490.57 | 1997 | 504.46 | 2018 | 518.55
72000 | 5217 | [18 empty] | 1634 | 288.36 | 1681 | 314.05 | 1727 | 340.14 | 1772 | 366.5 | 1795 | 380.32 | 1817 | 393.7 | 1839 | 407.27 | 1861 | 421.03 | 1882 | 434.28 | 1904 | 448.41 | 1925 | 462.02 | 1946 | 475.8 | 1967 | 489.77 | 1988 | 503.93 | 2008 | 517.52
74000 | 5362 | [18 empty] | 1653 | 298.57 | 1698 | 324.01 | 1743 | 350.38 | 1788 | 377.66 | 1810 | 391.31 | 1832 | 405.16 | 1853 | 418.54 | 1875 | 432.79 | 1896 | 446.53 | 1917 | 460.44 | 1938 | 474.53 | 1959 | 488.8 | 1979 | 502.49 | 2000 | 517.12 | 2020 | 531.15
76000 | 5507 | [36 empty] | 1931 | 473.02 | 1951 | 486.86 | 1972 | 501.61 | 1992 | 515.77 | 2012 | 530.1
78000 | 5652 | [36 empty] | 1945 | 485.43 | 1966 | 500.5 | 1986 | 515 | 2006 | 529.66 | 2025 | 543.68
80000 | 5797 | [36 empty] | 1960 | 498.48 | 1980 | 513.26 | 2000 | 528.23 | 2020 | 543.37
82000 | 5942 | [36 empty] | 1976 | 512.21 | 1995 | 526.68 | 2015 | 542.12
84000 | 6087 | [36 empty] | 1992 | 525.91 | 2011 | 540.82
86000 | 6232 | [36 empty] | 2008 | 539.57 | 2027 | 554.93
88000 | 6377 | [36 empty] | 2025 | 554.05
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 5450HPB
5450HPB — Backward Curved High Pressure Fan
Outlet Area: 16.92 ft² Wheel Diameter: 54.25" Tip Speed (FPM): 14.2 x RPM
Max. RPM — Design 14: 986 Design 17: 1338 Design 22: 1549 Design 26: 1831
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
25000 | 1478 | 453 | 10.01 | 592 | 20.44
27500 | 1625 | 469 | 11.16 | 600 | 22.06 | 717 | 34.54
30000 | 1773 | 487 | 12.49 | 611 | 23.91 | 722 | 36.79
32500 | 1921 | 506 | 13.95 | 624 | 25.92 | 730 | 39.28 | 829 | 54.09
35000 | 2069 | 527 | 15.65 | 638 | 27.99 | 740 | 41.95 | 834 | 57.03
37500 | 2216 | 548 | 17.45 | 654 | 30.29 | 752 | 44.87 | 842 | 60.34 | 928 | 77.14
40000 | 2364 | 570 | 19.43 | 671 | 32.76 | 764 | 47.68 | 852 | 63.91 | 934 | 80.97 | 1014 | 99.46
42500 | 2512 | 593 | 21.66 | 689 | 35.43 | 779 | 50.98 | 863 | 67.6 | 943 | 85.29 | 1019 | 103.9 | 1093 | 123.68
45000 | 2660 | 617 | 24.15 | 708 | 38.34 | 794 | 54.24 | 875 | 71.4 | 952 | 89.47 | 1026 | 108.62 | 1098 | 128.95 | 1167 | 149.98
47500 | 2807 | 641 | 26.8 | 727 | 41.34 | 810 | 57.71 | 889 | 75.58 | 964 | 94.35 | 1035 | 113.73 | 1104 | 134.26 | 1171 | 155.67 | 1236 | 177.95
50000 | 2955 | 666 | 29.76 | 748 | 44.79 | 827 | 61.43 | 903 | 79.69 | 976 | 99.11 | 1045 | 119.02 | 1112 | 139.95 | 1177 | 161.84 | 1240 | 184.39
52500 | 3103 | 690 | 32.76 | 769 | 48.37 | 846 | 65.68 | 919 | 84.3 | 989 | 104.05 | 1057 | 124.84 | 1122 | 146.21 | 1184 | 168.03 | 1246 | 191.4
55000 | 3251 | 715 | 36.1 | 791 | 52.28 | 865 | 70.05 | 935 | 88.92 | 1004 | 109.53 | 1069 | 130.54 | 1132 | 152.31 | 1193 | 174.82 | 1253 | 198.47 | 1311 | 222.61 | 1368 | 247.58 | 1424 | 273.48
57500 | 3398 | 741 | 39.8 | 814 | 56.56 | 884 | 74.53 | 952 | 93.88 | 1019 | 114.97 | 1083 | 136.83 | 1144 | 159.06 | 1204 | 182.32 | 1261 | 205.68 | 1318 | 230.54 | 1373 | 255.65 | 1428 | 282.07 | 1481 | 308.72
60000 | 3546 | 766 | 43.56 | 837 | 61.04 | 905 | 79.65 | 970 | 99.21 | 1034 | 120.39 | 1097 | 143.03 | 1157 | 166.09 | 1215 | 189.67 | 1271 | 213.68 | 1326 | 238.6 | 1380 | 264.42 | 1433 | 290.89 | 1485 | 318 | 1511 | 332.06 | 1536 | 345.79
62500 | 3694 | 792 | 47.72 | 860 | 65.73 | 926 | 84.93 | 989 | 104.98 | 1051 | 126.54 | 1111 | 149.16 | 1170 | 172.97 | 1227 | 197.31 | 1282 | 222.01 | 1336 | 247.55 | 1388 | 273.34 | 1440 | 300.49 | 1490 | 327.53 | 1515 | 341.48 | 1540 | 355.74 | 1565 | 370.33 | 1589 | 384.54 | 1613 | 399.07
65000 | 3842 | [18 empty] | 1346 | 256.31 | 1397 | 282.62 | 1447 | 309.62 | 1497 | 337.93 | 1521 | 351.82 | 1546 | 366.68 | 1570 | 381.14 | 1594 | 395.89 | 1617 | 410.18
67500 | 3989 | [18 empty] | 1357 | 265.45 | 1407 | 292.3 | 1456 | 319.77 | 1505 | 348.54 | 1528 | 362.36 | 1552 | 377.15 | 1576 | 392.23 | 1599 | 406.82 | 1622 | 421.67 | 1645 | 436.8 | 1668 | 452.22 | 1691 | 467.95 | 1713 | 483.16 | 1735 | 498.66
70000 | 4137 | [18 empty] | 1369 | 274.99 | 1418 | 302.41 | 1466 | 330.36 | 1513 | 358.84 | 1537 | 373.91 | 1560 | 388.58 | 1583 | 403.54 | 1605 | 417.99 | 1628 | 433.46 | 1651 | 449.21 | 1673 | 464.39 | 1695 | 479.84 | 1717 | 495.55 | 1739 | 511.56 | 1761 | 527.86 | 1782 | 543.55 | 1803 | 559.52
72500 | 4285 | [18 empty] | 1382 | 284.96 | 1430 | 312.96 | 1477 | 341.44 | 1523 | 370.35 | 1546 | 385.25 | 1568 | 399.69 | 1591 | 415.18 | 1613 | 430.2 | 1635 | 445.52 | 1657 | 461.09 | 1679 | 476.88 | 1701 | 492.94 | 1722 | 508.36 | 1744 | 524.94 | 1765 | 540.88 | 1786 | 557.08 | 1807 | 573.53 | 1828 | 590.29
75000 | 4433 | [18 empty] | 1395 | 294.76 | 1443 | 324.01 | 1489 | 353.02 | 1534 | 382.38 | 1556 | 397.1 | 1578 | 412.09 | 1600 | 427.37 | 1622 | 442.93 | 1643 | 457.95 | 1665 | 474.09 | 1686 | 489.67 | 1707 | 505.49 | 1728 | 521.54 | 1749 | 537.81 | 1770 | 554.33 | 1791 | 571.08 | 1811 | 587.15
77500 | 4580 | [18 empty] | 1409 | 305.07 | 1456 | 334.88 | 1501 | 364.4 | 1545 | 394.21 | 1567 | 409.51 | 1588 | 424.28 | 1610 | 440.12 | 1631 | 455.41 | 1652 | 470.97 | 1673 | 486.79 | 1694 | 502.89 | 1715 | 519.28 | 1736 | 535.95 | 1756 | 551.96 | 1776 | 568.16 | 1797 | 585.54 | 1817 | 602.19
80000 | 4728 | [18 empty] | 1424 | 315.95 | 1469 | 345.58 | 1514 | 376.33 | 1557 | 406.6 | 1578 | 421.7 | 1600 | 437.86 | 1621 | 453.47 | 1642 | 469.34 | 1662 | 484.59 | 1683 | 500.99 | 1703 | 516.74 | 1724 | 533.67 | 1744 | 549.95 | 1764 | 566.5 | 1784 | 583.32 | 1804 | 600.4 | 1823 | 616.66
82500 | 4876 | [18 empty] | 1439 | 326.81 | 1483 | 356.88 | 1527 | 388.07 | 1570 | 419.57 | 1591 | 435.29 | 1611 | 450.42 | 1632 | 466.6 | 1653 | 483.06 | 1673 | 498.89 | 1693 | 514.95 | 1713 | 531.26 | 1733 | 547.83 | 1753 | 564.64 | 1772 | 580.75 | 1792 | 598.08 | 1811 | 614.68 | 1831 | 632.57
85000 | 5024 | [18 empty] | 1455 | 338.35 | 1498 | 368.83 | 1541 | 400.44 | 1583 | 432.35 | 1603 | 447.86 | 1624 | 464.42 | 1644 | 480.37 | 1664 | 496.54 | 1684 | 512.95 | 1704 | 529.59 | 1724 | 546.48 | 1743 | 562.66 | 1763 | 580.05 | 1782 | 596.7 | 1801 | 613.58 | 1820 | 630.71
87500 | 5171 | [18 empty] | 1471 | 349.93 | 1514 | 381.51 | 1555 | 412.72 | 1597 | 445.8 | 1617 | 461.9 | 1637 | 478.25 | 1657 | 494.8 | 1677 | 511.6 | 1696 | 527.7 | 1716 | 544.94 | 1735 | 561.47 | 1754 | 578.21 | 1773 | 595.19 | 1792 | 612.4 | 1811 | 629.85 | 1830 | 647.53
90000 | 5319 | [18 empty] | 1488 | 362.29 | 1529 | 393.45 | 1570 | 425.75 | 1611 | 459.15 | 1631 | 475.84 | 1650 | 491.88 | 1670 | 509.04 | 1689 | 525.53 | 1709 | 543.16 | 1728 | 560.07 | 1747 | 577.2 | 1766 | 594.55 | 1784 | 611.09 | 1803 | 628.89 | 1821 | 645.85
92500 | 5467 | [18 empty] | 1505 | 374.78 | 1546 | 406.98 | 1586 | 439.58 | 1625 | 472.42 | 1645 | 489.67 | 1664 | 506.27 | 1684 | 524.04 | 1703 | 541.12 | 1722 | 558.43 | 1741 | 575.95 | 1759 | 592.69 | 1778 | 610.66 | 1796 | 627.79 | 1814 | 645.12
95000 | 5615 | [36 empty] | 1754 | 591.63 | 1772 | 608.98 | 1790 | 626.51 | 1808 | 644.24 | 1826 | 662.18
97500 | 5762 | [36 empty] | 1767 | 607.14 | 1785 | 625.06 | 1803 | 643.19 | 1821 | 661.54
100000 | 5910 | [36 empty] | 1781 | 623.56 | 1799 | 642.04 | 1817 | 660.77
102500 | 6058 | [36 empty] | 1796 | 640.94 | 1814 | 660.02 | 1831 | 678.25
105000 | 6206 | [36 empty] | 1811 | 658.31 | 1828 | 676.86
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 6000HPB
6000HPB — Backward Curved High Pressure Fan
Outlet Area: 20.7 ft² Wheel Diameter: 60.00" Tip Speed (FPM): 15.71 x RPM
Max. RPM — Design 14: 891 Design 17: 1082 Design 22: 1401 Design 26: 1655
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
30000 | 1449 | 407 | 11.99 | 534 | 24.61
33000 | 1594 | 421 | 13.36 | 541 | 26.58
36000 | 1739 | 437 | 14.94 | 550 | 28.71 | 652 | 44.44
39000 | 1884 | 453 | 16.59 | 561 | 31.06 | 658 | 47.26 | 748 | 65.11
42000 | 2029 | 471 | 18.53 | 574 | 33.66 | 666 | 50.31 | 753 | 68.87
45000 | 2174 | 490 | 20.69 | 587 | 36.21 | 676 | 53.68 | 759 | 72.61 | 838 | 93.13
48000 | 2319 | 510 | 23.11 | 602 | 39.14 | 688 | 57.43 | 767 | 76.69 | 843 | 97.71 | 915 | 119.77
51000 | 2464 | 530 | 25.67 | 617 | 42.12 | 700 | 61.07 | 777 | 81.22 | 850 | 102.65 | 920 | 125.42
54000 | 2609 | 550 | 28.4 | 634 | 45.6 | 713 | 64.92 | 788 | 85.95 | 858 | 107.72 | 925 | 130.72 | 991 | 155.47
57000 | 2754 | 572 | 31.63 | 651 | 49.2 | 727 | 69.01 | 799 | 90.54 | 868 | 113.39 | 933 | 136.94 | 996 | 161.82 | 1057 | 187.7
60000 | 2899 | 593 | 34.89 | 669 | 53.14 | 742 | 73.43 | 812 | 95.7 | 878 | 118.9 | 942 | 143.41 | 1003 | 168.74 | 1062 | 195.07 | 1120 | 222.72
63000 | 3043 | 615 | 38.54 | 688 | 57.47 | 758 | 78.23 | 825 | 100.81 | 890 | 125.08 | 951 | 149.71 | 1011 | 175.89 | 1068 | 202.57 | 1124 | 230.49 | 1179 | 259.61
66000 | 3188 | 637 | 42.41 | 707 | 61.96 | 774 | 83.14 | 839 | 106.27 | 902 | 131.13 | 962 | 156.78 | 1020 | 183.36 | 1076 | 210.82 | 1130 | 239.05 | 1183 | 268.29 | 1235 | 298.58
69000 | 3333 | 660 | 46.73 | 727 | 66.89 | 792 | 88.83 | 854 | 112.15 | 915 | 137.53 | 973 | 163.69 | 1030 | 191.19 | 1084 | 218.86 | 1137 | 247.78 | 1189 | 277.88 | 1240 | 308.88 | 1289 | 340.04
72000 | 3478 | 682 | 51.09 | 747 | 72.04 | 810 | 94.69 | 870 | 118.52 | 929 | 144.37 | 986 | 171.46 | 1041 | 199.4 | 1094 | 227.91 | 1145 | 256.89 | 1196 | 287.68 | 1245 | 318.73 | 1293 | 350.48 | 1341 | 383.83 | 1364 | 400.29
75000 | 3623 | 705 | 55.93 | 768 | 77.73 | 828 | 100.71 | 886 | 125.02 | 943 | 151.21 | 999 | 179.17 | 1052 | 207.43 | 1104 | 236.77 | 1154 | 266.47 | 1203 | 297.14 | 1251 | 328.79 | 1299 | 362.07 | 1345 | 395.12 | 1368 | 412.21 | 1391 | 429.71 | 1413 | 446.68 | 1435 | 464.06
78000 | 3768 | [18 empty] | 1212 | 307.85 | 1259 | 340.05 | 1305 | 373.11 | 1350 | 406.78 | 1373 | 424.59 | 1395 | 441.84 | 1417 | 459.45 | 1439 | 477.44 | 1460 | 494.82
81000 | 3913 | [18 empty] | 1222 | 319.12 | 1268 | 351.9 | 1313 | 385.43 | 1357 | 419.69 | 1378 | 436.41 | 1400 | 454.39 | 1422 | 472.72 | 1443 | 490.39 | 1464 | 508.41
84000 | 4058 | [18 empty] | 1232 | 330.17 | 1277 | 363.52 | 1321 | 397.51 | 1364 | 432.13 | 1385 | 449.53 | 1406 | 467.3 | 1427 | 485.39 | 1448 | 503.8 | 1469 | 522.52
87000 | 4203 | [18 empty] | 1243 | 341.8 | 1287 | 375.76 | 1330 | 410.24 | 1372 | 445.23 | 1393 | 463.28 | 1414 | 481.71 | 1434 | 499.48 | 1454 | 517.61 | 1475 | 537.12 | 1495 | 555.85 | 1515 | 574.88 | 1535 | 594.22 | 1555 | 613.9 | 1574 | 632.71 | 1594 | 653.07 | 1613 | 672.55 | 1632 | 692.37 | 1651 | 712.56
90000 | 4348 | [18 empty] | 1255 | 354.07 | 1298 | 388.65 | 1340 | 423.65 | 1381 | 459.06 | 1402 | 477.79 | 1422 | 495.86 | 1442 | 514.28 | 1462 | 533.05 | 1481 | 551.08 | 1501 | 570.57 | 1521 | 590.36 | 1540 | 609.28 | 1559 | 628.5 | 1579 | 649.2 | 1598 | 669.01 | 1617 | 689.14 | 1635 | 708.3 | 1654 | 729.07
93000 | 4493 | [18 empty] | 1267 | 366.17 | 1309 | 401.32 | 1350 | 436.83 | 1391 | 473.64 | 1411 | 492.05 | 1431 | 510.79 | 1450 | 528.8 | 1470 | 548.23 | 1489 | 566.88 | 1508 | 585.87 | 1527 | 605.2 | 1546 | 624.86 | 1565 | 644.83 | 1584 | 665.08 | 1603 | 685.61 | 1621 | 705.14 | 1640 | 726.29
96000 | 4638 | [18 empty] | 1279 | 378.14 | 1321 | 414.71 | 1361 | 450.74 | 1401 | 487.98 | 1421 | 507.09 | 1440 | 525.45 | 1459 | 544.12 | 1479 | 564.24 | 1497 | 582.4 | 1516 | 602.04 | 1535 | 622.01 | 1554 | 642.33 | 1572 | 661.76 | 1590 | 681.5 | 1609 | 702.82 | 1627 | 723.11 | 1645 | 743.66
99000 | 4783 | [18 empty] | 1293 | 391.8 | 1333 | 427.94 | 1373 | 465.42 | 1412 | 503.12 | 1431 | 521.88 | 1450 | 540.94 | 1469 | 560.31 | 1488 | 579.99 | 1507 | 600 | 1525 | 619.12 | 1543 | 638.54 | 1562 | 659.53 | 1580 | 679.59 | 1598 | 699.97 | 1615 | 719.32 | 1633 | 740.35 | 1651 | 761.66
102000 | 4928 | [18 empty] | 1306 | 404.54 | 1346 | 442.03 | 1385 | 479.91 | 1423 | 518.02 | 1442 | 537.52 | 1461 | 557.3 | 1480 | 577.41 | 1498 | 596.63 | 1516 | 616.14 | 1534 | 635.93 | 1552 | 656.02 | 1570 | 676.4 | 1588 | 697.12 | 1606 | 718.14 | 1623 | 738.15 | 1640 | 758.42
105000 | 5072 | [18 empty] | 1320 | 418.22 | 1359 | 456.07 | 1398 | 495.33 | 1435 | 533.8 | 1454 | 554.04 | 1472 | 573.42 | 1490 | 593.07 | 1509 | 614.22 | 1526 | 633.21 | 1544 | 653.71 | 1562 | 674.49 | 1579 | 694.27 | 1597 | 715.68 | 1614 | 736.02 | 1631 | 756.65 | 1648 | 777.57
108000 | 5217 | [18 empty] | 1335 | 432.91 | 1373 | 471.09 | 1411 | 510.69 | 1448 | 550.54 | 1466 | 570.37 | 1484 | 590.47 | 1502 | 610.88 | 1520 | 631.57 | 1537 | 651.25 | 1555 | 672.5 | 1572 | 692.71 | 1589 | 713.18 | 1606 | 733.92 | 1623 | 754.94 | 1640 | 776.25
111000 | 5362 | [36 empty] | 1566 | 691.03 | 1583 | 711.96 | 1600 | 733.17 | 1616 | 753.25 | 1633 | 774.96 | 1650 | 796.98
114000 | 5507 | [36 empty] | 1577 | 709.3 | 1594 | 730.97 | 1611 | 752.92 | 1627 | 773.69 | 1644 | 796.15
117000 | 5652 | [36 empty] | 1589 | 728.7 | 1605 | 749.7 | 1622 | 772.39 | 1638 | 793.88 | 1654 | 815.61
120000 | 5797 | [36 empty] | 1601 | 747.92 | 1617 | 769.62 | 1634 | 793.03 | 1650 | 815.27
123000 | 5942 | [36 empty] | 1614 | 768.42 | 1630 | 790.82 | 1646 | 813.5
126000 | 6087 | [36 empty] | 1627 | 788.86 | 1642 | 810.45
129000 | 6232 | [36 empty] | 1640 | 809.25 | 1655 | 831.49
132000 | 6377 | [36 empty] | 1654 | 831.12
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 6600HPB
6600HPB — Backward Curved High Pressure Fan
Outlet Area: 25.04 ft² Wheel Diameter: 66.00" Tip Speed (FPM): 17.28 x RPM
Max. RPM — Design 14: 810 Design 17: 984 Design 22: 1273 Design 26: 1504
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
30000 | 1198 | 352 | 12.01
33000 | 1318 | 360 | 13.17
36000 | 1438 | 369 | 14.38 | 485 | 29.59
39000 | 1558 | 380 | 15.81 | 490 | 31.53
42000 | 1677 | 391 | 17.24 | 496 | 33.55 | 591 | 52.38
45000 | 1797 | 403 | 18.85 | 504 | 35.89 | 595 | 55.2
48000 | 1917 | 416 | 20.66 | 513 | 38.37 | 600 | 58.08 | 681 | 79.82
51000 | 2037 | 429 | 22.54 | 522 | 40.78 | 606 | 61.11 | 685 | 83.64
54000 | 2157 | 443 | 24.66 | 532 | 43.39 | 614 | 64.64 | 689 | 87.2 | 761 | 111.87
57000 | 2276 | 458 | 27.04 | 543 | 46.25 | 622 | 68.08 | 695 | 91.3 | 765 | 116.62
60000 | 2396 | 473 | 29.53 | 554 | 49.13 | 631 | 71.76 | 702 | 95.68 | 769 | 121.1 | 834 | 148.46
63000 | 2516 | 488 | 32.16 | 566 | 52.34 | 640 | 75.36 | 710 | 100.36 | 775 | 126.25 | 838 | 154.11 | 898 | 182.95
66000 | 2636 | 504 | 35.13 | 579 | 55.91 | 650 | 79.27 | 718 | 104.94 | 781 | 131.27 | 842 | 159.44 | 901 | 189.08
70000 | 2796 | 525 | 39.27 | 597 | 61.03 | 665 | 85.1 | 730 | 111.46 | 791 | 138.76 | 850 | 167.64 | 907 | 198.06 | 962 | 229.55
74000 | 2955 | 547 | 43.94 | 615 | 66.35 | 680 | 91.01 | 743 | 118.31 | 802 | 146.56 | 859 | 176.18 | 914 | 207.11 | 967 | 239.19 | 1019 | 272.71 | 1070 | 307.83
78000 | 3115 | 569 | 48.92 | 634 | 72.2 | 696 | 97.46 | 756 | 125.09 | 814 | 154.7 | 869 | 185.07 | 923 | 217.2 | 974 | 249.66 | 1024 | 283.62 | 1074 | 319.68 | 1121 | 355.3
82000 | 3275 | [18 empty] | 1079 | 331.84 | 1125 | 368.28 | 1171 | 406.84
86000 | 3435 | [18 empty] | 1085 | 344.19 | 1130 | 381.63 | 1175 | 420.96 | 1218 | 460.14 | 1239 | 479.94
90000 | 3594 | [18 empty] | 1092 | 356.89 | 1136 | 395.23 | 1180 | 435.49 | 1222 | 475.35 | 1243 | 495.97 | 1264 | 517.1 | 1284 | 537.5
94000 | 3754 | [18 empty] | 1101 | 371.19 | 1144 | 410.28 | 1186 | 450.33 | 1227 | 491 | 1247 | 511.34 | 1268 | 533.36 | 1288 | 554.6 | 1308 | 576.29 | 1327 | 597.14
98000 | 3914 | [18 empty] | 1111 | 386.21 | 1152 | 424.98 | 1193 | 465.62 | 1233 | 507.02 | 1253 | 528.38 | 1273 | 550.14 | 1292 | 570.99 | 1312 | 593.59 | 1331 | 615.26 | 1350 | 637.37 | 1369 | 659.92 | 1388 | 682.95 | 1406 | 704.94
102000 | 4073 | [18 empty] | 1121 | 400.92 | 1162 | 441.55 | 1202 | 482.87 | 1241 | 524.81 | 1260 | 545.84 | 1279 | 567.32 | 1298 | 589.17 | 1317 | 611.42 | 1336 | 634.04 | 1355 | 657.08 | 1373 | 679.06 | 1392 | 702.94 | 1410 | 725.74 | 1428 | 748.97 | 1446 | 772.62
106000 | 4233 | [18 empty] | 1132 | 416.37 | 1172 | 457.8 | 1211 | 499.78 | 1249 | 542.23 | 1268 | 564.11 | 1287 | 586.46 | 1305 | 607.87 | 1324 | 631.13 | 1342 | 653.37 | 1360 | 675.95 | 1378 | 698.86 | 1396 | 722.16 | 1414 | 745.86 | 1432 | 769.94 | 1449 | 792.8 | 1467 | 817.71 | 1484 | 841.38 | 1501 | 865.46
110000 | 4393 | [18 empty] | 1144 | 432.65 | 1183 | 474.91 | 1221 | 517.56 | 1258 | 560.57 | 1277 | 583.36 | 1295 | 605.22 | 1313 | 627.47 | 1331 | 650.16 | 1349 | 673.29 | 1367 | 696.85 | 1384 | 719.27 | 1402 | 743.59 | 1419 | 766.66 | 1437 | 791.71 | 1454 | 815.49 | 1471 | 839.63 | 1488 | 864.15
114000 | 4553 | [18 empty] | 1156 | 448.67 | 1194 | 491.68 | 1232 | 536.29 | 1268 | 579.86 | 1286 | 602.22 | 1304 | 624.96 | 1322 | 648.14 | 1339 | 670.22 | 1357 | 694.21 | 1374 | 717.09 | 1391 | 740.36 | 1408 | 764.04 | 1425 | 788.11 | 1442 | 812.54 | 1459 | 837.28 | 1476 | 862.39 | 1493 | 887.84
118000 | 4712 | [18 empty] | 1169 | 465.72 | 1206 | 509.38 | 1243 | 554.68 | 1279 | 600.19 | 1296 | 622.09 | 1314 | 645.79 | 1331 | 668.4 | 1348 | 691.38 | 1365 | 714.71 | 1382 | 738.45 | 1399 | 762.6 | 1416 | 787.12 | 1433 | 812.07 | 1449 | 835.74 | 1465 | 859.77 | 1482 | 885.91 | 1498 | 910.59
122000 | 4872 | [18 empty] | 1183 | 483.9 | 1219 | 528.18 | 1255 | 574.09 | 1290 | 620.19 | 1307 | 643.04 | 1324 | 666.23 | 1341 | 689.78 | 1358 | 713.67 | 1375 | 737.97 | 1391 | 761 | 1408 | 786.04 | 1424 | 809.78 | 1441 | 835.62 | 1457 | 860.12 | 1473 | 885 | 1489 | 910.23
126000 | 5032 | [18 empty] | 1196 | 500.86 | 1232 | 546.88 | 1267 | 593.28 | 1302 | 641.29 | 1319 | 665.14 | 1335 | 687.78 | 1352 | 712.31 | 1369 | 737.2 | 1385 | 760.82 | 1401 | 784.77 | 1417 | 809.07 | 1433 | 833.71 | 1449 | 858.71 | 1465 | 884.06 | 1481 | 909.81 | 1496 | 934.05
130000 | 5192 | [18 empty] | 1211 | 520.38 | 1246 | 566.88 | 1280 | 613.72 | 1314 | 662.14 | 1330 | 685.39 | 1347 | 710.57 | 1363 | 734.49 | 1380 | 760.38 | 1396 | 784.98 | 1412 | 809.88 | 1427 | 833.39 | 1443 | 858.96 | 1459 | 884.91 | 1474 | 909.36 | 1490 | 936.01
134000 | 5351 | [18 empty] | 1226 | 540.06 | 1260 | 586.93 | 1293 | 634.08 | 1327 | 684.33 | 1343 | 708.51 | 1359 | 733.05 | 1375 | 757.94 | 1391 | 783.17 | 1407 | 808.72 | 1422 | 832.88 | 1438 | 859.08 | 1453 | 883.81 | 1469 | 910.7 | 1484 | 936.07 | 1499 | 961.77
138000 | 5511 | [36 empty] | 1434 | 858.98 | 1449 | 884.39 | 1464 | 910.09 | 1479 | 936.09 | 1494 | 962.41
142000 | 5671 | [36 empty] | 1446 | 884.77 | 1461 | 911.15 | 1476 | 937.86 | 1490 | 962.95
146000 | 5831 | [36 empty] | 1458 | 910.33 | 1473 | 937.65 | 1487 | 963.35 | 1502 | 991.34
150000 | 5990 | [36 empty] | 1471 | 937.61 | 1485 | 963.91 | 1500 | 992.5
154000 | 6150 | [36 empty] | 1484 | 964.79 | 1498 | 991.99
158000 | 6310 | [36 empty] | 1497 | 991.9
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 7300HPB
7300HPB — Backward Curved High Pressure Fan
Outlet Area: 30.63 ft² Wheel Diameter: 73.00" Tip Speed (FPM): 19.11 x RPM
Max. RPM — Design 14: 735 Design 17: 890 Design 22: 1180 Design 26: 1360
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
40000 | 1306 | 325 | 16.01
45000 | 1469 | 336 | 18.01 | 439 | 36.67
50000 | 1632 | 349 | 20.3 | 446 | 40.02 | 533 | 62.74
55000 | 1796 | 364 | 23 | 456 | 43.99 | 538 | 67.52
60000 | 1959 | 380 | 26.03 | 466 | 47.78 | 544 | 72.22 | 617 | 99.32
65000 | 2122 | 397 | 29.43 | 478 | 52.04 | 553 | 77.82 | 622 | 105.51 | 688 | 135.72
70000 | 2285 | 415 | 33.28 | 492 | 56.96 | 563 | 83.64 | 629 | 112.19 | 692 | 143.14
75000 | 2449 | 434 | 37.63 | 506 | 61.95 | 574 | 89.7 | 638 | 119.66 | 698 | 151.16 | 755 | 184.23
80000 | 2612 | 453 | 42.3 | 521 | 67.47 | 586 | 96.08 | 647 | 126.85 | 705 | 159.36 | 761 | 194.13 | 814 | 229.78
85000 | 2775 | 472 | 47.31 | 537 | 73.57 | 599 | 102.94 | 658 | 134.97 | 714 | 168.6 | 768 | 204.16 | 819 | 240.63 | 869 | 279.08
90000 | 2938 | 492 | 52.99 | 554 | 80.34 | 613 | 110.38 | 670 | 143.52 | 724 | 178.26 | 776 | 214.62 | 826 | 252.51 | 874 | 291.6 | 921 | 332.36
95000 | 3102 | 513 | 59.41 | 572 | 87.83 | 628 | 118.53 | 683 | 152.66 | 735 | 188.4 | 785 | 225.58 | 833 | 263.92 | 880 | 304.29 | 926 | 346.5 | 970 | 389.01 | 1014 | 434.3
100000 | 3265 | 533 | 65.92 | 590 | 95.65 | 644 | 127.5 | 696 | 161.82 | 747 | 199.11 | 795 | 237.08 | 842 | 276.86 | 888 | 318.51 | 932 | 360.91 | 975 | 404.73 | 1017 | 449.69 | 1058 | 495.9
105000 | 3428 | 554 | 73.24 | 608 | 103.83 | 660 | 136.75 | 710 | 171.79 | 759 | 209.72 | 807 | 250.09 | 852 | 290.47 | 896 | 332.36 | 939 | 375.8 | 981 | 420.8 | 1022 | 466.95 | 1062 | 514.01 | 1101 | 562.04
110000 | 3591 | 575 | 81.07 | 627 | 112.95 | 677 | 146.91 | 725 | 182.69 | 772 | 221.14 | 818 | 261.99 | 863 | 304.79 | 905 | 346.91 | 947 | 391.48 | 988 | 437.4 | 1027 | 483.24 | 1066 | 531.27 | 1105 | 581.53 | 1124 | 606.79 | 1142 | 630.98 | 1161 | 657.44
115000 | 3754 | 597 | 89.85 | 646 | 122.55 | 694 | 157.41 | 741 | 194.63 | 786 | 233.52 | 831 | 275.7 | 874 | 318.84 | 916 | 363.45 | 956 | 407.98 | 996 | 454.9 | 1034 | 501.49 | 1072 | 550.51 | 1109 | 600.14 | 1128 | 626.54 | 1146 | 651.8 | 1164 | 677.63 | 1182 | 704.02 | 1200 | 730.98
120000 | 3918 | [18 empty] | 1004 | 471.95 | 1042 | 520.77 | 1079 | 570.44 | 1115 | 620.89 | 1133 | 646.9 | 1151 | 673.42 | 1169 | 700.43 | 1186 | 726.14 | 1204 | 754.22
125000 | 4081 | [18 empty] | 1014 | 491.39 | 1051 | 541.11 | 1087 | 591.49 | 1122 | 642.44 | 1139 | 667.88 | 1157 | 695.66 | 1174 | 722.17 | 1191 | 749.08 | 1208 | 776.49
130000 | 4244 | [18 empty] | 1024 | 510.46 | 1060 | 561.03 | 1095 | 612.07 | 1130 | 665.24 | 1147 | 691.78 | 1164 | 718.85 | 1180 | 744.61 | 1197 | 772.77 | 1214 | 801.48 | 1230 | 828.64 | 1246 | 856.21 | 1263 | 886.31 | 1279 | 914.77 | 1295 | 943.74 | 1311 | 973.21 | 1326 | 1000.89 | 1342 | 1031.33 | 1358 | 1062.32
135000 | 4407 | [18 empty] | 1035 | 530.62 | 1070 | 582.09 | 1105 | 635.57 | 1138 | 687.56 | 1155 | 715.23 | 1171 | 741.53 | 1188 | 770.25 | 1204 | 797.54 | 1220 | 825.37 | 1236 | 853.72 | 1252 | 882.56 | 1268 | 911.87 | 1284 | 941.58 | 1299 | 969.5 | 1315 | 1000.1 | 1330 | 1028.87 | 1346 | 1060.43
140000 | 4571 | [18 empty] | 1047 | 552.08 | 1081 | 604.39 | 1115 | 658.65 | 1148 | 713.05 | 1164 | 740.03 | 1180 | 767.48 | 1196 | 795.39 | 1212 | 823.82 | 1227 | 850.66 | 1243 | 880.06 | 1259 | 910.01 | 1274 | 938.32 | 1289 | 967.05 | 1305 | 998.52 | 1320 | 1028.11 | 1335 | 1058.1 | 1350 | 1088.46
145000 | 4734 | [18 empty] | 1059 | 573.37 | 1092 | 626.37 | 1125 | 681.3 | 1157 | 736.22 | 1173 | 764.36 | 1189 | 792.96 | 1205 | 822.07 | 1220 | 849.57 | 1236 | 879.63 | 1251 | 908.04 | 1266 | 936.92 | 1281 | 966.23 | 1296 | 996.05 | 1311 | 1026.33 | 1326 | 1057.15 | 1340 | 1085.99 | 1355 | 1117.63
150000 | 4897 | [18 empty] | 1071 | 594.57 | 1104 | 649.83 | 1136 | 705.34 | 1168 | 762.76 | 1183 | 790.18 | 1199 | 820.01 | 1214 | 848.24 | 1229 | 876.88 | 1244 | 905.94 | 1259 | 935.47 | 1274 | 965.42 | 1289 | 995.89 | 1304 | 1026.8 | 1318 | 1055.81 | 1333 | 1087.68 | 1347 | 1117.58
152500 | 4979 | [18 empty] | 1077 | 605.16 | 1110 | 661.51 | 1142 | 718.2 | 1173 | 774.9 | 1189 | 804.92 | 1204 | 833.34 | 1219 | 862.17 | 1234 | 891.42 | 1249 | 921.08 | 1264 | 951.22 | 1279 | 981.79 | 1293 | 1010.49 | 1308 | 1041.97 | 1322 | 1071.52 | 1336 | 1101.49 | 1351 | 1134.41
155000 | 5060 | [18 empty] | 1084 | 617.43 | 1116 | 673.18 | 1148 | 731.01 | 1179 | 788.93 | 1194 | 817.55 | 1209 | 846.58 | 1224 | 875.98 | 1239 | 905.84 | 1254 | 936.11 | 1268 | 964.58 | 1283 | 995.72 | 1297 | 1024.97 | 1312 | 1057.03 | 1326 | 1087.13 | 1340 | 1117.66 | 1354 | 1148.57
157500 | 5142 | [18 empty] | 1091 | 629.75 | 1122 | 684.81 | 1154 | 743.8 | 1184 | 800.87 | 1199 | 830.03 | 1214 | 859.65 | 1229 | 889.7 | 1244 | 920.14 | 1259 | 951.03 | 1273 | 980.09 | 1288 | 1011.85 | 1302 | 1041.69 | 1316 | 1071.93 | 1330 | 1102.55 | 1344 | 1133.63 | 1358 | 1165.15
160000 | 5224 | [18 empty] | 1098 | 642.13 | 1129 | 698.31 | 1160 | 756.54 | 1190 | 814.77 | 1205 | 844.53 | 1220 | 874.78 | 1235 | 905.45 | 1249 | 934.35 | 1264 | 965.85 | 1278 | 995.48 | 1292 | 1025.48 | 1307 | 1058.3 | 1321 | 1089.11 | 1335 | 1120.37 | 1348 | 1149.5
162500 | 5305 | [36 empty] | 1283 | 1010.74 | 1297 | 1041.34 | 1311 | 1072.34 | 1325 | 1103.71 | 1339 | 1135.54 | 1353 | 1167.75
165000 | 5387 | [36 empty] | 1288 | 1025.9 | 1302 | 1057.08 | 1316 | 1088.69 | 1330 | 1120.66 | 1344 | 1153.1 | 1357 | 1183.31
167500 | 5468 | [36 empty] | 1294 | 1043.31 | 1307 | 1072.72 | 1321 | 1104.9 | 1335 | 1137.53 | 1348 | 1167.95
170000 | 5550 | [36 empty] | 1299 | 1058.22 | 1313 | 1090.67 | 1326 | 1121.02 | 1340 | 1154.23 | 1353 | 1185.24
172500 | 5632 | [36 empty] | 1304 | 1073.02 | 1318 | 1106.06 | 1332 | 1139.52 | 1345 | 1170.79 | 1358 | 1202.44
175000 | 5713 | [36 empty] | 1310 | 1090.19 | 1323 | 1121.32 | 1337 | 1155.39 | 1350 | 1187.26
177500 | 5795 | [36 empty] | 1316 | 1107.31 | 1329 | 1139.03 | 1342 | 1171.12 | 1355 | 1203.57
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 8075HPB
7300HPB — Backward Curved High Pressure Fan
Outlet Area: 37.49 ft² Wheel Diameter: 80.75" Tip Speed (FPM): 21.14 x RPM
Max. RPM — Design 14: 663 Design 17: 804 Design 22: 1041 Design 26: 1230
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
50000 | 1334 | 295 | 19.91 | 394 | 41.94
55000 | 1467 | 304 | 22.09 | 397 | 44.89
60000 | 1600 | 313 | 24.24 | 402 | 48.21
65000 | 1734 | 324 | 26.89 | 409 | 52.08 | 484 | 80.15
70000 | 1867 | 335 | 29.63 | 416 | 55.81 | 488 | 84.82 | 556 | 117.52
75000 | 2001 | 348 | 33.04 | 424 | 59.78 | 494 | 90.22 | 559 | 123.59
80000 | 2134 | 360 | 36.32 | 433 | 64.1 | 500 | 95.42 | 563 | 129.89 | 622 | 166.59
85000 | 2267 | 373 | 40.06 | 443 | 68.84 | 508 | 101.6 | 568 | 136.45 | 625 | 174.05
90000 | 2401 | 387 | 44.33 | 453 | 73.64 | 516 | 107.61 | 574 | 143.49 | 629 | 181.83 | 682 | 222.79
95000 | 2534 | 401 | 48.86 | 464 | 79.03 | 525 | 114.13 | 581 | 151.06 | 634 | 189.99 | 685 | 231.51 | 735 | 276.04
100000 | 2667 | 415 | 53.66 | 476 | 85.11 | 534 | 120.59 | 589 | 159.21 | 640 | 198.79 | 690 | 241.67 | 738 | 286.5 | 784 | 332.78
105000 | 2801 | 430 | 59.14 | 488 | 91.37 | 544 | 127.73 | 597 | 167.18 | 647 | 208.29 | 695 | 251.41 | 741 | 296.35 | 787 | 344.91
110000 | 2934 | 445 | 64.95 | 501 | 98.41 | 554 | 134.94 | 606 | 175.86 | 655 | 218.55 | 701 | 261.93 | 746 | 307.94 | 790 | 356.46 | 833 | 407.03
115000 | 3067 | 460 | 71.09 | 513 | 105.08 | 565 | 143.01 | 615 | 184.47 | 663 | 228.61 | 708 | 273.32 | 752 | 320.43 | 794 | 368.65 | 836 | 420.22 | 876 | 472.01
120000 | 3201 | 475 | 77.58 | 527 | 113.23 | 576 | 151.26 | 625 | 193.98 | 671 | 238.46 | 715 | 284.46 | 758 | 332.64 | 800 | 383.09 | 840 | 434.23 | 880 | 488.46 | 918 | 542.46
125000 | 3334 | 490 | 84.43 | 540 | 121.02 | 588 | 160.5 | 635 | 203.57 | 680 | 249.25 | 723 | 296.53 | 765 | 345.87 | 806 | 397.25 | 845 | 449.09 | 883 | 502.55 | 921 | 558.84 | 958 | 616.41
130000 | 3468 | [18 empty] | 888 | 519.26 | 925 | 576.36 | 961 | 634.35 | 996 | 693.26 | 1014 | 724.91
135000 | 3601 | [18 empty] | 893 | 535.45 | 929 | 593.07 | 964 | 651.56 | 999 | 712.72 | 1016 | 743.29 | 1033 | 774.61 | 1050 | 806.69
140000 | 3734 | [18 empty] | 899 | 553.09 | 934 | 611 | 968 | 669.93 | 1002 | 731.41 | 1019 | 763.16 | 1036 | 795.59 | 1052 | 826.4 | 1068 | 857.86 | 1085 | 892.5
145000 | 3868 | [18 empty] | 906 | 572.28 | 940 | 630.54 | 973 | 689.58 | 1006 | 751.44 | 1023 | 784.46 | 1039 | 815.77 | 1055 | 847.72 | 1071 | 880.28 | 1087 | 913.54
150000 | 4001 | [18 empty] | 912 | 589.22 | 946 | 649.73 | 979 | 710.99 | 1011 | 772.84 | 1027 | 804.81 | 1043 | 837.44 | 1059 | 870.63 | 1075 | 904.44 | 1090 | 936.31 | 1105 | 968.75 | 1121 | 1004.48 | 1136 | 1038.21 | 1151 | 1072.56 | 1166 | 1107.62
155000 | 4134 | [18 empty] | 920 | 609.72 | 953 | 670.63 | 985 | 732.03 | 1017 | 796.13 | 1032 | 826.82 | 1048 | 860.6 | 1063 | 892.62 | 1078 | 925.16 | 1094 | 960.82 | 1109 | 994.48 | 1124 | 1028.69 | 1139 | 1063.53 | 1154 | 1098.97 | 1168 | 1132.15 | 1183 | 1168.92 | 1197 | 1203.33 | 1211 | 1238.33
160000 | 4268 | [18 empty] | 927 | 627.9 | 960 | 691.19 | 991 | 752.69 | 1022 | 816.64 | 1038 | 850.83 | 1053 | 883.25 | 1068 | 916.29 | 1083 | 950.02 | 1098 | 984.38 | 1113 | 1019.29 | 1127 | 1052 | 1142 | 1088 | 1157 | 1124.62 | 1171 | 1158.89 | 1185 | 1193.72 | 1200 | 1232.16 | 1214 | 1268.21 | 1228 | 1304.89
165000 | 4401 | [18 empty] | 936 | 649.84 | 967 | 711.4 | 998 | 775.23 | 1029 | 841.57 | 1044 | 874.45 | 1059 | 907.99 | 1074 | 942.15 | 1088 | 974.28 | 1103 | 1009.74 | 1117 | 1043.09 | 1132 | 1079.88 | 1146 | 1114.33 | 1160 | 1149.27 | 1174 | 1184.71 | 1188 | 1220.64 | 1202 | 1257.17 | 1216 | 1294.23 | 1230 | 1331.93
170000 | 4535 | [18 empty] | 944 | 669.51 | 975 | 733.46 | 1006 | 799.81 | 1036 | 866.16 | 1050 | 897.66 | 1065 | 932.31 | 1079 | 964.93 | 1094 | 1000.84 | 1108 | 1034.64 | 1122 | 1069.03 | 1136 | 1103.99 | 1150 | 1139.61 | 1164 | 1175.84 | 1178 | 1212.52 | 1192 | 1249.72 | 1206 | 1287.5 | 1219 | 1322.53
175000 | 4668 | [18 empty] | 953 | 691.13 | 983 | 755.23 | 1013 | 821.65 | 1043 | 890.37 | 1057 | 923.03 | 1072 | 958.89 | 1086 | 992.67 | 1100 | 1027.01 | 1114 | 1061.89 | 1128 | 1097.4 | 1142 | 1133.47 | 1156 | 1170.22 | 1169 | 1204.47 | 1183 | 1242.4 | 1196 | 1277.76 | 1210 | 1316.81 | 1223 | 1353.08
180000 | 4801 | [18 empty] | 962 | 712.66 | 992 | 779.08 | 1021 | 845.54 | 1050 | 914.2 | 1064 | 948.03 | 1079 | 985.13 | 1093 | 1020.05 | 1106 | 1052.72 | 1120 | 1088.73 | 1134 | 1125.33 | 1148 | 1162.6 | 1161 | 1197.34 | 1174 | 1232.62 | 1188 | 1271.65 | 1201 | 1308.02 | 1214 | 1345.02 | 1227 | 1382.56
185000 | 4935 | [18 empty] | 971 | 734.15 | 1001 | 802.86 | 1030 | 871.71 | 1058 | 940.26 | 1072 | 975.34 | 1086 | 1010.91 | 1100 | 1047.07 | 1113 | 1080.85 | 1127 | 1118.06 | 1140 | 1152.84 | 1154 | 1191.22 | 1167 | 1227.07 | 1180 | 1263.45 | 1193 | 1300.37 | 1206 | 1337.79 | 1219 | 1375.84
190000 | 5068 | [18 empty] | 981 | 757.94 | 1010 | 826.52 | 1038 | 895.13 | 1066 | 966.02 | 1080 | 1002.3 | 1094 | 1039.14 | 1107 | 1073.67 | 1121 | 1111.57 | 1134 | 1147.04 | 1147 | 1182.94 | 1160 | 1219.39 | 1173 | 1256.36 | 1186 | 1293.81 | 1199 | 1331.86 | 1212 | 1370.41 | 1225 | 1409.59
195000 | 5201 | [36 empty] | 1154 | 1212.67 | 1167 | 1250.31 | 1180 | 1288.42 | 1193 | 1327.07 | 1205 | 1362.92 | 1218 | 1402.62
200000 | 5335 | [36 empty] | 1162 | 1245.15 | 1174 | 1280.73 | 1187 | 1320.11 | 1200 | 1359.96 | 1212 | 1396.92 | 1224 | 1434.31
205000 | 5468 | [36 empty] | 1169 | 1274 | 1182 | 1314.07 | 1194 | 1351.28 | 1207 | 1392.36 | 1219 | 1430.48
210000 | 5601 | [36 empty] | 1177 | 1305.75 | 1190 | 1347.09 | 1202 | 1385.53 | 1214 | 1424.33 | 1226 | 1463.64
215000 | 5735 | [36 empty] | 1186 | 1340.51 | 1198 | 1379.69 | 1210 | 1419.34 | 1222 | 1459.45
220000 | 5868 | [36 empty] | 1194 | 1371.72 | 1206 | 1412.04 | 1218 | 1452.86 | 1230 | 1494.11
225000 | 6002 | [36 empty] | 1203 | 1406.2 | 1215 | 1447.7 | 1226 | 1486.03
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).

## 8900HPB
8900HPB — Backward Curved High Pressure Fan
Outlet Area: 45.54 ft² Wheel Diameter: 89.00" Tip Speed (FPM): 23.3 x RPM
Max. RPM — Design 14: 602 Design 17: 730 Design 22: 944 Design 26: 1116
CFM | OV (FPM) | 2" SP |  | 4" SP |  | 6" SP |  | 8" SP |  | 10" SP |  | 12" SP |  | 14" SP |  | 16" SP |  | 18" SP |  | 20" SP |  | 22" SP |  | 24" SP |  | 26" SP |  | 27" SP |  | 28" SP |  | 29" SP |  | 30" SP |  | 31" SP |  | 32" SP |  | 33" SP |  | 34" SP |  | 35" SP |  | 36" SP |  | 37" SP |  | 38" SP |  | 39" SP |  | 40" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
70000 | 1537 | 280 | 28.18 | 363 | 56.89
75000 | 1647 | 288 | 30.73 | 367 | 60.25 | 438 | 94.21
80000 | 1757 | 296 | 33.33 | 372 | 63.97 | 440 | 98.53
85000 | 1866 | 304 | 36.02 | 377 | 67.55 | 443 | 103.19
90000 | 1976 | 313 | 39.15 | 384 | 72.11 | 447 | 108.26 | 506 | 148.22
95000 | 2086 | 323 | 42.79 | 390 | 76.03 | 452 | 113.91 | 509 | 154.64
100000 | 2196 | 332 | 46.16 | 397 | 80.49 | 457 | 119.41 | 513 | 161.61 | 565 | 205.98
105000 | 2306 | 342 | 50.09 | 405 | 85.59 | 463 | 125.54 | 517 | 168.33 | 568 | 214.09 | 617 | 262.93
110000 | 2415 | 352 | 54.2 | 412 | 90.1 | 469 | 131.54 | 521 | 174.84 | 571 | 221.77 | 619 | 271.74
115000 | 2525 | 363 | 58.98 | 421 | 96.03 | 475 | 137.43 | 527 | 183.19 | 575 | 230.24 | 622 | 281.47 | 666 | 333.42
120000 | 2635 | 374 | 64.02 | 429 | 101.41 | 482 | 144.12 | 532 | 190.34 | 580 | 239.72 | 625 | 290.73 | 668 | 343.56
125000 | 2745 | 384 | 68.77 | 438 | 107.63 | 490 | 151.73 | 538 | 198.38 | 584 | 247.76 | 629 | 300.95 | 671 | 354.81 | 713 | 413.03
130000 | 2855 | 396 | 74.85 | 447 | 114.01 | 497 | 158.46 | 545 | 207.4 | 590 | 258.15 | 633 | 310.93 | 674 | 365.53 | 715 | 424.49 | 754 | 484.23
135000 | 2964 | 407 | 80.65 | 457 | 121.34 | 505 | 166.22 | 551 | 215.21 | 595 | 267.03 | 638 | 322.17 | 678 | 377.4 | 718 | 437.2 | 756 | 497.35
140000 | 3074 | 418 | 86.72 | 466 | 128.07 | 513 | 174.09 | 558 | 224.13 | 601 | 277.06 | 643 | 333.2 | 682 | 389.03 | 721 | 449.32 | 759 | 511.97 | 795 | 574.43
145000 | 3184 | 429 | 93.07 | 476 | 135.81 | 522 | 183.15 | 566 | 234.28 | 608 | 288.34 | 648 | 343.98 | 687 | 402.14 | 725 | 462.86 | 762 | 526.07 | 798 | 590.93 | 833 | 657.43
150000 | 3294 | [18 empty] | 800 | 604.65 | 835 | 673.39 | 869 | 743.65
155000 | 3404 | [18 empty] | 803 | 619.97 | 837 | 688.77 | 870 | 758.62 | 903 | 832.27
160000 | 3513 | [18 empty] | 807 | 636.99 | 840 | 705.96 | 873 | 778.28 | 905 | 851.43 | 920 | 886.52 | 936 | 925.43
165000 | 3623 | [18 empty] | 811 | 653.74 | 844 | 725.02 | 875 | 794.62 | 907 | 870.07 | 922 | 906.2 | 938 | 946.15 | 953 | 984.06 | 968 | 1022.84
170000 | 3733 | [18 empty] | 816 | 672.62 | 847 | 741.02 | 879 | 815.71 | 909 | 888.02 | 925 | 928.25 | 940 | 966.38 | 955 | 1005.31 | 969 | 1041.89 | 984 | 1082.55
175000 | 3843 | [18 empty] | 820 | 688.76 | 852 | 761.95 | 882 | 833.37 | 912 | 908.15 | 927 | 946.64 | 942 | 985.89 | 957 | 1025.96 | 971 | 1063.59 | 986 | 1105.33 | 1000 | 1144.57 | 1014 | 1184.64
180000 | 3953 | [18 empty] | 826 | 709.69 | 856 | 779.94 | 886 | 853.48 | 916 | 930.54 | 930 | 967.32 | 945 | 1007.83 | 959 | 1045.9 | 974 | 1088 | 988 | 1127.55 | 1002 | 1167.82 | 1016 | 1208.92 | 1030 | 1250.81 | 1044 | 1293.57
185000 | 4062 | [18 empty] | 831 | 727.78 | 861 | 800.34 | 891 | 876.22 | 920 | 952.54 | 934 | 990.36 | 948 | 1029.02 | 962 | 1068.36 | 976 | 1108.33 | 990 | 1149.04 | 1004 | 1190.44 | 1018 | 1232.61 | 1032 | 1275.58 | 1045 | 1315.62 | 1059 | 1360.24 | 1072 | 1401.83
190000 | 4172 | [18 empty] | 836 | 745.57 | 866 | 820.48 | 895 | 895.7 | 924 | 974.16 | 938 | 1013.09 | 952 | 1052.79 | 966 | 1093.34 | 980 | 1134.73 | 993 | 1173.21 | 1007 | 1215.88 | 1021 | 1259.3 | 1034 | 1299.74 | 1047 | 1340.84 | 1061 | 1386.51 | 1074 | 1429.12 | 1087 | 1472.5 | 1100 | 1516.61
195000 | 4282 | [18 empty] | 842 | 765.76 | 872 | 843.17 | 900 | 917.85 | 928 | 995.46 | 942 | 1035.43 | 956 | 1076.22 | 970 | 1117.86 | 983 | 1156.83 | 997 | 1200.15 | 1010 | 1240.53 | 1023 | 1281.5 | 1037 | 1326.92 | 1050 | 1369.18 | 1063 | 1412.17 | 1076 | 1455.81 | 1089 | 1500.24 | 1101 | 1541.19 | 1114 | 1587.06
200000 | 4392 | [18 empty] | 848 | 785.7 | 877 | 862.72 | 905 | 939.68 | 933 | 1019.63 | 947 | 1060.78 | 960 | 1099.32 | 974 | 1142.07 | 987 | 1182.1 | 1000 | 1222.82 | 1013 | 1264.35 | 1026 | 1306.61 | 1039 | 1349.42 | 1052 | 1392.86 | 1065 | 1437.01 | 1078 | 1481.8 | 1091 | 1527.31 | 1103 | 1569.29 | 1116 | 1616.24
205000 | 4502 | [18 empty] | 855 | 808.28 | 883 | 884.91 | 911 | 964.38 | 938 | 1043.5 | 951 | 1082.43 | 965 | 1125.52 | 978 | 1165.86 | 991 | 1206.95 | 1004 | 1248.8 | 1017 | 1291.35 | 1030 | 1334.68 | 1043 | 1378.87 | 1055 | 1419.66 | 1068 | 1465.05 | 1081 | 1511.12 | 1093 | 1553.62 | 1106 | 1601.04
210000 | 4611 | [18 empty] | 861 | 827.86 | 889 | 906.85 | 916 | 985.62 | 943 | 1067.07 | 957 | 1110.59 | 970 | 1151.42 | 983 | 1192.91 | 996 | 1235.18 | 1008 | 1274.34 | 1021 | 1317.98 | 1034 | 1362.46 | 1046 | 1403.67 | 1059 | 1449.64 | 1071 | 1492.25 | 1084 | 1539.65 | 1096 | 1583.33 | 1108 | 1627.64
215000 | 4721 | [18 empty] | 868 | 850.25 | 895 | 928.59 | 922 | 1009.76 | 949 | 1093.71 | 962 | 1135.03 | 975 | 1176.99 | 988 | 1219.7 | 1000 | 1259.31 | 1013 | 1303.38 | 1026 | 1348.21 | 1038 | 1389.8 | 1050 | 1432.06 | 1063 | 1479.15 | 1075 | 1522.83 | 1087 | 1567.15 | 1099 | 1612.19 | 1111 | 1657.71
220000 | 4831 | [36 empty] | 1030 | 1374.13 | 1042 | 1416.79 | 1055 | 1464.27 | 1067 | 1508.27 | 1079 | 1553.03 | 1091 | 1598.42 | 1103 | 1644.6 | 1114 | 1686.9
230000 | 5051 | [36 empty] | 1040 | 1432.91 | 1052 | 1477.84 | 1064 | 1523.49 | 1076 | 1569.74 | 1087 | 1612.24 | 1099 | 1659.82 | 1110 | 1703.52
240000 | 5270 | [36 empty] | 1051 | 1494.47 | 1062 | 1537.5 | 1074 | 1585.46 | 1085 | 1629.6 | 1097 | 1678.87 | 1108 | 1724.19
250000 | 5490 | [36 empty] | 1062 | 1554.69 | 1074 | 1604.57 | 1085 | 1650.56 | 1096 | 1697.09 | 1107 | 1744.08
260000 | 5709 | [36 empty] | 1074 | 1618.09 | 1085 | 1665.89 | 1096 | 1714.19 | 1107 | 1763.14
270000 | 5929 | [36 empty] | 1087 | 1685.21 | 1098 | 1735.4 | 1109 | 1786.14
280000 | 6148 | [36 empty] | 1100 | 1752.03 | 1111 | 1804.44
Underlined values in the original catalog indicate maximum static efficiency; underline markers are not reproduced here (formatting not recoverable from source).
Performance is for BCS with outlet duct and with or without inlet duct.
BHP is fan shaft brake horsepower and does not include belt drive losses.
Blank cells indicate no rated point published in the source catalog for that CFM / SP combination (values are never estimated).