## Panel Fan
JOB ORDER
JOB ORDER# | : |  | AFBM-JO2600048 | [10 empty] | Date |  | : |  | 2026-07-07
|  | __________________________________________ | [14 empty] | _________________________________
Project | : |  |  |  | 10 |  | pcs. |  | 42 |  | " Ø |  | EWF |  | ( |  | Standard |  | )
_________________________________________________________________________________________
Target Date: |  | 2026-07-07 | [5 empty] | Date Started: | [8 empty] | Date Finished:
| ____________________ | [9 empty] | ____________________ | [8 empty] | ____________________
PRODUCTION LEAD TIME |  |  |  |  | Body |  | 38 |  | days |  | Body |  | 15 | days
[7 empty] | _____ | [5 empty] | _____
Orientation | : | Exhaust 1 | [11 empty] | Impeller |  | : | Paddle Type
|  | ___________________________________ | [14 empty] | _____________________________
Mounting | : | Wall Mounted | [11 empty] | Drive |  | : | Belt
|  | ___________________________________ | [14 empty] | _____________________________
Capacity | : | [8 empty] | 28782 cfm @ 0" w.g.
_______________________________________________________________________________
Speed | : |  |  |  | rpm |  |  | 815 |  | rpm
_______________________________________________________________________________
Drive Motor | : |  | HP, | 3 | PH, | 220 |  | V, | 60 | Hz, | 4 | pole, | 1745 | rpm, | Foot Mounted |  |  |  | , | TECO | TEFC
_______________________________________________________________________________
Motor Pulley | : |  |  | "Ø x |  | 2B |  | x | 28 | mm Ø bore |  |  | x | 8 | mm keyway |  |  |  |  | 64 | mm Ø Hub
_______________________________________________________________________________
Fan Pulley | : |  |  | "Ø x |  | 2B |  | x | 1 1/2”Ø bore x 3/8" keyway | [10 empty] | 75 | mm Ø Hub
_______________________________________________________________________________
Hub | : | 3”Ø x 3”L x 1 1/2”Ø bore x 3/8” keyway
_______________________________________________________________________________
Shafting | : |  | 1 1/2”Ø bore x 3/8" keyway
_______________________________________________________________________________
Belt | :
_______________________________________________________________________________
Bearing | : | [7 empty] | -- | 20 | pcs
_______________________________________________________________________________
/afbm rev 6 : 03/28/2026
1
1
2
2

## Source
Panel Fan | [5 empty] | Brand | TECO | Hyundai | TECO_1Phase | TECO_3Phase | Hyundai_3Phase | Single Phase, 4 pole, 60Hz, TECO | Single Phase, 4 pole, 60Hz | RPM | Shaft Diameter | Keyway | HP | Phase | Pole | Pulley
Blade Diameter | Bore Size | Hub Details | Shafting | Bearing | Shaft | TECO | TECO_1Phase | Hyundai_3Phase | 1/4 HP, 1PH, TECO | 1/2 HP, 3PH, TECO | 1/2 HP, 3PH, Hyundai |  | 1/4 HP, 1PH, TECO | 1715 | 14 | 5 | 0.25 | 1 | 4 | 1A
10 | 1”Ø bore x 5/16" keyway | 2” Ø x 2” L x 1"Ø bore x 5/16” keyway | 1"Ø x 5/16” keyway | UCP205 | 1 | Hyundai | TECO_3Phase |  | 1/2 HP, 1PH, TECO | 1 HP, 3PH, TECO | 1 HP, 3PH, Hyundai |  | 1/2 HP, 1PH, TECO | 1750 | 19 | 6 | 0.5 | 1 | 4 | 1A
12 | 1”Ø bore x 5/16" keyway | 2” Ø x 2” L x 1"Ø bore x 5/16” keyway | 1"Ø x 5/16” keyway | UCP205 | 1 |  |  |  | 3 /4 HP, 1PH, TECO | 1 1/2 HP, 3PH, TECO | 1 1/2 HP, 3PH, Hyundai |  | 3 /4 HP, 1PH, TECO | 1750 | 19 | 6 | 0.75 | 1 | 4 | 1A
14 | 1”Ø bore x 5/16" keyway | 2” Ø x 2” L x 1"Ø bore x 5/16” keyway | 1"Ø x 5/16” keyway | UCP205 | 1 |  |  |  | 1 HP, 1PH, TECO | 2 HP, 3PH, TECO | 2 HP, 3PH, Hyundai |  | 1 HP, 1PH, TECO | 1750 | 24 | 8 | 1 | 1 | 4 | 2A
16 | 1 1/4”Ø bore x 3/8" keyway | 2 1/2”Ø x 2 1/2”L x 1 1/4"Ø bore x 3/8” keyway | 1 1/4"Ø x 3/8” keyway | UCP207 | 1.25 |  |  |  | 1.5 HP, 1PH, TECO | 3 HP, 3PH, TECO | 3 HP, 3PH, Hyundai |  | 1.5 HP, 1PH, TECO | 1750 | 24 | 8 | 1.5 | 1 | 4 | 2B
18 | 1 1/4”Ø bore x 3/8" keyway | 2 1/2”Ø x 2 1/2”L x 1 1/4"Ø bore x 3/8” keyway | 1 1/4"Ø x 3/8” keyway | UCP207 | 1.25 |  |  |  | 2 HP, 1PH, TECO | 5 HP, 3PH, TECO | 5.5 HP, 3PH, Hyundai |  | 2 HP, 1PH, TECO | 1750 | 28 | 8 | 2 | 1 | 4 | 2B
20 | 1 1/4”Ø bore x 3/8" keyway | 2 1/2”Ø x 2 1/2”L x 1 1/4"Ø bore x 3/8” keyway | 1 1/4"Ø x 3/8” keyway | UCP207 | 1.25 |  |  |  | 3 HP, 1PH, TECO | 7 1/2 HP, 3PH, TECO | 7 1/2 HP, 3PH, Hyundai |  | 3 HP, 1PH, TECO | 1750 | 28 | 8 | 3 | 1 | 4 | 2B
24 | 1 1/4”Ø bore x 3/8" keyway | 2 1/2”Ø x 2 1/2”L x 1 1/4"Ø bore x 3/8” keyway | 1 1/4"Ø x 3/8” keyway | UCP207 | 1.25 |  |  |  | 5 HP, 1PH, TECO | 10 HP, 3PH, TECO | 10 HP, 3PH, Hyundai |  | 5 HP, 1PH, TECO | 1750 | 28 | 8 | 5 | 1 | 4 | 2B
30 | 1 1/4”Ø bore x 3/8" keyway | 2 1/2”Ø x 2 1/2”L x 1 1/4"Ø bore x 3/8” keyway | 1 1/4"Ø x 3/8” keyway | UCP207 | 1.25 |  |  |  |  | 15 HP, 3PH, TECO | 15 HP, 3PH, Hyundai | Three Phase, 4 pole, 60Hz, TECO | 1/2 HP, 3PH, TECO | 1680 | 14 | 5 | 0.5 | 3 | 4 | 1A
36 | 1 1/2”Ø bore x 3/8" keyway | 3”Ø x 3”L x 1 1/2”Ø bore x 3/8” keyway | 1 1/2”Ø x 3/8” keyway | UCP208 | 1.5 |  |  |  |  | 20 HP, 3PH, TECO | 20 HP, 3PH, Hyundai |  | 1 HP, 3PH, TECO | 1710 | 19 | 6 | 1 | 3 | 4 | 2A
42 | 1 1/2”Ø bore x 3/8" keyway | 3”Ø x 3”L x 1 1/2”Ø bore x 3/8” keyway | 1 1/2”Ø x 3/8” keyway | UCP208 | 1.5 |  |  |  |  | 25 HP, 3PH, TECO | 25 HP, 3PH, Hyundai |  | 1 1/2 HP, 3PH, TECO | 1720 | 24 | 8 | 1.5 | 3 | 4 | 2B
48 | 1 3/4”Ø bore x 1/2" keyway | 3 1/2” Ø x 3 1/2” L x 1 3/4"Ø bore x 1/2” keyway | 1 3/4 x 1/2” keyway | UCP209 | 1.75 |  |  |  |  | 30 HP, 3PH, TECO | 30 HP, 3PH, Hyundai |  | 2 HP, 3PH, TECO | 1715 | 24 | 8 | 2 | 3 | 4 | 2B
54 | 1 3/4”Ø bore x 1/2" keyway | 3 1/2” Ø x 3 1/2” L x 1 3/4"Ø bore x 1/2” keyway | 1 3/4 x 1/2” keyway | UCP209 | 1.75 |  |  |  |  | 40 HP, 3PH, TECO | 40 HP, 3PH, Hyundai |  | 3 HP, 3PH, TECO | 1735 | 28 | 8 | 3 | 3 | 4 | 2B
60 | 2 ”Ø x 1/2" keyway | 4”Ø x 4”L x 2 1/4"Ø bore x 1/2” keyway | 2"Ø x 1/2” keyway | UCP211 | 2 |  |  |  |  | 50 HP, 3PH, TECO | 50 HP, 3PH, Hyundai |  | 5 HP, 3PH, TECO | 1745 | 28 | 8 | 5 | 3 | 4 | 2B
[10 empty] | 60 HP, 3PH, TECO | 60 HP, 3PH, Hyundai |  | 7 1/2 HP, 3PH, TECO | 1750 | 38 | 10 | 7.5 | 3 | 4 | 2B
[10 empty] | 75 HP, 3PH, TECO | 75 HP, 3PH, Hyundai |  | 10 HP, 3PH, TECO | 1750 | 38 | 10 | 10 | 3 | 4 | 3B
[10 empty] | 100 HP, 3PH, TECO | 100 HP, 3PH, Hyundai |  | 15 HP, 3PH, TECO | 1760 | 42 | 12 | 15 | 3 | 4 | 3B
[10 empty] | 125 HP, 3PH, TECO | 125 HP, 3PH, Hyundai |  | 20 HP, 3PH, TECO | 1760 | 42 | 12 | 20 | 3 | 4 | 3C
[10 empty] | 150 HP, 3PH, TECO | 150 HP, 3PH, Hyundai |  | 25 HP, 3PH, TECO | 1760 | 48 | 14 | 25 | 3 | 4 | 3C
[10 empty] | 175 HP, 3PH, TECO | 180 HP, 3PH, Hyundai |  | 30 HP, 3PH, TECO | 1765 | 48 | 14 | 30 | 3 | 4 | 4C
[10 empty] | 200 HP, 3PH, TECO | 200 HP, 3PH, Hyundai |  | 40 HP, 3PH, TECO | 1760 | 55 | 16 | 40 | 3 | 4 | 5C
[10 empty] | 250 HP, 3PH, TECO | 270 HP, 3PH, Hyundai |  | 50 HP, 3PH, TECO | 1770 | 60 | 18 | 50 | 3 | 4 | 6C
[10 empty] | 300 HP, 3PH, TECO | 340 HP, 3PH, Hyundai |  | 60 HP, 3PH, TECO | 1765 | 60 | 18 | 60 | 3 | 4 | 6C
[13 empty] | 75 HP, 3PH, TECO | 1775 | 65 | 18 | 75 | 3 | 4 | 6C
[5 empty] | TECO | [7 empty] | 100 HP, 3PH, TECO | 1775 | 75 | 20 | 100 | 3 | 4 | 6C
Propeller | Make |  |  |  | TECO_3_Phase | [7 empty] | 125 HP, 3PH, TECO | 1770 | 75 | 20 | 125 | 3 | 4 | 6C
Kidney Type | Standard |  |  |  | 1 | [7 empty] | 150 HP, 3PH, TECO | 1770 | 85 | 22 | 150 | 3 | 4 | 6C
Paddle Type | Customized | [11 empty] | 175 HP, 3PH, TECO | 1770 | 85 | 22 | 175 | 3 | 4 | 6C
Airfoil | Client Design | [11 empty] | 200 HP, 3PH, TECO | 1775 | 95 | 25 | 200 | 3 | 4 | 6C
[13 empty] | 250 HP, 3PH, TECO | 1775 | 95 | 25 | 250 | 3 | 4 | 6C
[13 empty] | 300 HP, 3PH, TECO | 1775 | 95 | 25 | 300 | 3 | 4 | 6C
Drive | [11 empty] | Three Phase, 4 pole, 60Hz, Hyundai | 1/2 HP, 3PH, Hyundai | 1660 | 14 | 5 | 0.5 | 3 | 4 | 1A
Direct | [12 empty] | 1 HP, 3PH, Hyundai | 1668 | 19 | 6 | 1 | 3 | 4 | 2A
Belt | [12 empty] | 1 1/2 HP, 3PH, Hyundai | 1680 | 24 | 8 | 1.5 | 3 | 4 | 2B
Directly Coupled | [12 empty] | 2 HP, 3PH, Hyundai | 1680 | 24 | 8 | 2 | 3 | 4 | 2B
[13 empty] | 3 HP, 3PH, Hyundai | 1716 | 28 | 8 | 3 | 3 | 4 | 2B
[13 empty] | 5.5 HP, 3PH, Hyundai | 1728 | 28 | 8 | 5.5 | 3 | 4 | 2B
Motor Phase | Voltage | Frequency | Pole | Mounting | Enclosure | [7 empty] | 7 1/2 HP, 3PH, Hyundai | 1728 | 38 | 10 | 7.5 | 3 | 4 | 2B
1 | 220 | 60 | 2 | Foot Mounted | TEFC | [7 empty] | 10 HP, 3PH, Hyundai | 1728 | 38 | 10 | 10 | 3 | 4 | 3B
3 | 380 | 50 | 4 | Flange Mounted | Exproof | [7 empty] | 15 HP, 3PH, Hyundai | 1728 | 42 | 12 | 15 | 3 | 4 | 3B
| 440 |  | 6 | [9 empty] | 20 HP, 3PH, Hyundai | 1752 | 42 | 12 | 20 | 3 | 4 | 3C
|  |  | 8 | [9 empty] | 25 HP, 3PH, Hyundai | 1752 | 48 | 14 | 25 | 3 | 4 | 3C
[13 empty] | 30 HP, 3PH, Hyundai | 1764 | 48 | 14 | 30 | 3 | 4 | 4C
[13 empty] | 40 HP, 3PH, Hyundai | 1764 | 55 | 16 | 40 | 3 | 4 | 5C
Mounting | Fan Type | Orientation | [10 empty] | 50 HP, 3PH, Hyundai | 1764 | 55 | 16 | 50 | 3 | 4 | 6C
Wall Mounted | EWF | Exhaust 1 | [10 empty] | 60 HP, 3PH, Hyundai | 1770 | 55 | 16 | 60 | 3 | 4 | 6C
Ceiling Mounted | FAWF | Exhaust 2 | [10 empty] | 75 HP, 3PH, Hyundai | 1770 | 60 | 18 | 75 | 3 | 4 | 6C
With Stand |  | Supply 1 | [10 empty] | 100 HP, 3PH, Hyundai | 1776 | 75 | 20 | 100 | 3 | 4 | 6C
Ceiling Hang |  | Supply 2 | [10 empty] | 125 HP, 3PH, Hyundai | 1776 | 75 | 20 | 125 | 3 | 4 | 6C
[13 empty] | 150 HP, 3PH, Hyundai | 1776 | 80 | 22 | 150 | 3 | 4 | 6C
[13 empty] | 180 HP, 3PH, Hyundai | 1776 | 80 | 22 | 180 | 3 | 4 | 6C
[13 empty] | 200 HP, 3PH, Hyundai | 1776 | 80 | 22 | 200 | 3 | 4 | 6C
[13 empty] | 270 HP, 3PH, Hyundai | 1776 | 80 | 22 | 270 | 3 | 4 | 6C
[13 empty] | 340 HP, 3PH, Hyundai | 1788 | 95 | 25 | 340 | 3 | 4 | 6C
Rotation
Clockwise
Counterclockwise
Clockwise & Counterclockwise
Header Details |  | Legend:
Date | 2026-07-07 | Red - Editable
Job Order # | AFBM-JO2600048
Project | EWF
Make | Standard
Target Date | 2026-07-07
Quantity | 10
UOM | pcs.
Body Lead Time | 38
Blade Lead Time | 15
Input Fan/Blower Details Here |  | Fan/Blower Details
Type | EWF | Computed Fan RPM | 814.3333
Blade Diameter | 42 | Shafting | 1 1/2”Ø x 3/8” keyway
Orientation | Exhaust 1 | Bearing | UCP208
Mounting | Wall Mounted | Hub | 3”Ø x 3”L x 1 1/2”Ø bore x 3/8” keyway
Blade Type | Paddle Type | Shafting | 1 1/2”Ø bore x 3/8" keyway
Drive Type | Belt | Shaft in inches | 1.5
Capacity | 25015 cfm @ 0.36" w.g.
Test at 0" w.g. | 28782 cfm @ 0" w.g.
RPM (Catalogue) | 811
Input Motor Details Here |  | Motor Details
Motor Brand | TECO | Motor HP | 5
Motor PH (Alias) | TECO_3Phase | Motor PH | 3
Motor HP | 5 HP, 3PH, TECO | Motor RPM | 1745
Voltage | 220 | Pole | 4
Frequency | 60 | Motor Shaft | 28
Mounting | Foot Mounted | Motor Keyway | 8
Enclosure | TEFC | Motor Pulley | 2B
Motor RPM | 1745 | Motor Pulley Hub | 64
RPM (Catalogue) | 811 | Fan Pulley Hub | 75
Motor Pulley | 3.5
Fan Pulley | 7.5
Computed Fan RPM | 814.3333