## Contents
AEROVENT FANS & BLOWERS
Backward Inclined Centrifugal Fans — Catalog 300 (Engineering & Performance Data)
Sheet | Contents | Source pages
Performance SWSI | RPM & BHP grids — single width, single inlet (sizes 122–982 COMPLETE) | 18–20
Performance DWDI | RPM & BHP grids — double width, double inlet (sizes 122–890 COMPLETE) | 29–35
Dimensional Data | Arrangement / class dimensional tables (pending) | 36–65
Typical Specifications | SWSI & DWDI specification text (pending) | 66–67
Performance basis: standard air, 0.075 lb/ft³ (70°F, sea level, 29.92" Hg).
Power rating (BHP) excludes transmission losses and accessory effects. Type B & D installation (free/ducted inlet, ducted outlet).

## Performance SWSI
PERFORMANCE — BC SWSI (Single Width, Single Inlet)
Standard air 0.075 lb/ft³. BHP excludes drive/accessory losses. RPM and BHP shown per static pressure (" w.g.). Class legend: I=regular left of II band; II=light band; III=italic right; IV=dark band (formatting not reproduced here — use Max RPM by class to bound selections).
1225CEB
Outlet Area 0.86 ft² ¦ Wheel Dia. 12.25 in ¦ Tip Speed 3.21 × RPM (ft/min) ¦ Max BHP = 0.076 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 3167 Class II — 4119 Class III — 4600 (Selections above 4000 RPM not recommended — consult factory)
CFM | OV | 0.25" SP |  | 0.5" SP |  | 0.75" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 2.5" SP |  | 3" SP |  | 3.5" SP |  | 4" SP |  | 4.5" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
688 | 800 | 869 | 0.05 | 1044 | 0.08 | 1195 | 0.12 | 1335 | 0.17
774 | 900 | 931 | 0.06 | 1096 | 0.1 | 1240 | 0.14 | 1370 | 0.18
860 | 1000 | 994 | 0.07 | 1152 | 0.12 | 1289 | 0.16 | 1413 | 0.21 | 1642 | 0.31
946 | 1100 | 1058 | 0.09 | 1210 | 0.13 | 1342 | 0.18 | 1461 | 0.23 | 1677 | 0.34 | 1879 | 0.46
1032 | 1200 | 1123 | 0.11 | 1271 | 0.16 | 1397 | 0.21 | 1512 | 0.26 | 1720 | 0.37 | 1911 | 0.49 | 2093 | 0.63
1204 | 1400 | 1256 | 0.15 | 1397 | 0.21 | 1514 | 0.26 | 1622 | 0.32 | 1816 | 0.45 | 1992 | 0.58 | 2158 | 0.72 | 2317 | 0.87 | 2471 | 1.03
1376 | 1600 | 1396 | 0.2 | 1525 | 0.27 | 1638 | 0.33 | 1738 | 0.4 | 1922 | 0.54 | 2088 | 0.68 | 2244 | 0.83 | 2390 | 0.98 | 2532 | 1.15 | 2671 | 1.33 | 2805 | 1.51
1548 | 1800 | 1539 | 0.27 | 1655 | 0.34 | 1765 | 0.42 | 1861 | 0.49 | 2035 | 0.64 | 2193 | 0.79 | 2340 | 0.95 | 2480 | 1.12 | 2612 | 1.29 | 2741 | 1.48 | 2866 | 1.67
1720 | 2000 | 1685 | 0.36 | 1790 | 0.43 | 1893 | 0.51 | 1988 | 0.6 | 2154 | 0.76 | 2305 | 0.93 | 2445 | 1.1 | 2578 | 1.27 | 2705 | 1.46 | 2827 | 1.65 | 2944 | 1.85
1892 | 2200 | 1834 | 0.46 | 1929 | 0.54 | 2024 | 0.63 | 2116 | 0.72 | 2277 | 0.9 | 2421 | 1.08 | 2556 | 1.26 | 2683 | 1.45 | 2805 | 1.65 | 2922 | 1.84 | 3035 | 2.05
2064 | 2400 | 1984 | 0.58 | 2072 | 0.66 | 2159 | 0.76 | 2245 | 0.86 | 2403 | 1.06 | 2542 | 1.25 | 2671 | 1.45 | 2794 | 1.65 | 2911 | 1.86 | 3023 | 2.06 | 3132 | 2.28
2236 | 2600 | 2135 | 0.72 | 2216 | 0.81 | 2297 | 0.91 | 2377 | 1.01 | 2531 | 1.23 | 2667 | 1.44 | 2791 | 1.66 | 2909 | 1.87 | 3023 | 2.09 | 3131 | 2.31 | 3236 | 2.54
2408 | 2800 | 2287 | 0.88 | 2363 | 0.98 | 2438 | 1.08 | 2512 | 1.19 | 2659 | 1.42 | 2793 | 1.66 | 2915 | 1.89 | 3028 | 2.11 | 3138 | 2.35 | 3243 | 2.58 | 3344 | 2.82
2580 | 3000 | 2439 | 1.07 | 2511 | 1.17 | 2581 | 1.28 | 2650 | 1.4 | 2789 | 1.64 | 2921 | 1.89 | 3040 | 2.14 | 3151 | 2.38 | 3256 | 2.63 | 3358 | 2.88 | 3457 | 3.13
2752 | 3200 | 2593 | 1.28 | 2660 | 1.39 | 2726 | 1.51 | 2791 | 1.63 | 2922 | 1.88 | 3049 | 2.15 | 3167 | 2.41 | 3276 | 2.68 | 3378 | 2.94 | 3477 | 3.2 | 3572 | 3.47
2924 | 3400 | 2746 | 1.52 | 2810 | 1.64 | 2872 | 1.76 | 2934 | 1.89 | 3057 | 2.15 | 3179 | 2.43 | 3295 | 2.72 | 3402 | 2.99 | 3503 | 3.27 | 3599 | 3.55 | 3691 | 3.83
Low-pressure range
CFM | OV | 5" SP |  | 5.5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1720 | 2000 | 3059 | 2.05 | 3172 | 2.26 | 3283 | 2.48 | 3500 | 2.94
1892 | 2200 | 3144 | 2.26 | 3250 | 2.48 | 3355 | 2.71 | 3559 | 3.18 | 3758 | 3.67
2064 | 2400 | 3238 | 2.5 | 3340 | 2.73 | 3440 | 2.96 | 3633 | 3.44 | 3821 | 3.95 | 4006 | 4.48 | 4186 | 5.04
2236 | 2600 | 3337 | 2.77 | 3436 | 3 | 3533 | 3.25 | 3719 | 3.75 | 3898 | 4.27 | 4073 | 4.81 | 4245 | 5.37 | 4413 | 5.96 | 4578 | 6.56
2408 | 2800 | 3442 | 3.06 | 3538 | 3.31 | 3631 | 3.56 | 3812 | 4.08 | 3985 | 4.61 | 4152 | 5.17 | 4315 | 5.74 | 4476 | 6.34
2580 | 3000 | 3552 | 3.39 | 3645 | 3.64 | 3735 | 3.9 | 3910 | 4.44 | 4079 | 5 | 4240 | 5.57 | 4397 | 6.16 | 4551 | 6.77
2752 | 3200 | 3665 | 3.74 | 3756 | 4.01 | 3843 | 4.28 | 4013 | 4.83 | 4176 | 5.4 | 4335 | 6 | 4487 | 6.61
2924 | 3400 | 3781 | 4.11 | 3870 | 4.4 | 3955 | 4.69 | 4120 | 5.26 | 4279 | 5.86 | 4433 | 6.47 | 4582 | 7.09
3096 | 3600 | 3901 | 4.52 | 3986 | 4.82 | 4070 | 5.12 | 4231 | 5.73 | 4386 | 6.34 | 4535 | 6.97
3268 | 3800 | 4023 | 4.96 | 4106 | 5.27 | 4187 | 5.59 | 4345 | 6.23 | 4496 | 6.87
3440 | 4000 | 4147 | 5.43 | 4228 | 5.76 | 4307 | 6.09 | 4461 | 6.75
3612 | 4200 | 4272 | 5.93 | 4352 | 6.28 | 4430 | 6.62 | 4579 | 7.31
High-pressure range
1350CEB
Outlet Area 1.05 ft² ¦ Wheel Dia. 13.50 in ¦ Tip Speed 3.53 × RPM (ft/min) ¦ Max BHP = 0.124 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 2874 Class II — 3738 Class III — 4600 (Selections above 4000 RPM not recommended — consult factory)
CFM | OV | 0.25" SP |  | 0.5" SP |  | 0.75" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 2.5" SP |  | 3" SP |  | 3.5" SP |  | 4" SP |  | 4.5" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
840 | 800 | 791 | 0.06 | 949 | 0.1 | 1086 | 0.15 | 1213 | 0.2
945 | 900 | 847 | 0.08 | 997 | 0.12 | 1127 | 0.17 | 1245 | 0.23
1050 | 1000 | 905 | 0.09 | 1048 | 0.14 | 1172 | 0.19 | 1285 | 0.25 | 1491 | 0.38
1155 | 1100 | 963 | 0.11 | 1102 | 0.17 | 1220 | 0.22 | 1328 | 0.28 | 1524 | 0.41 | 1707 | 0.56
1260 | 1200 | 1022 | 0.13 | 1157 | 0.19 | 1271 | 0.25 | 1375 | 0.32 | 1563 | 0.45 | 1736 | 0.6 | 1901 | 0.77
1470 | 1400 | 1144 | 0.18 | 1272 | 0.25 | 1378 | 0.32 | 1475 | 0.4 | 1651 | 0.54 | 1811 | 0.7 | 1960 | 0.88 | 2105 | 1.06 | 2244 | 1.26
1680 | 1600 | 1272 | 0.25 | 1388 | 0.33 | 1491 | 0.41 | 1582 | 0.49 | 1748 | 0.65 | 1899 | 0.83 | 2039 | 1.01 | 2172 | 1.2 | 2300 | 1.4 | 2426 | 1.62 | 2548 | 1.85
1890 | 1800 | 1403 | 0.33 | 1508 | 0.42 | 1607 | 0.51 | 1695 | 0.6 | 1851 | 0.78 | 1995 | 0.97 | 2128 | 1.16 | 2254 | 1.37 | 2374 | 1.58 | 2490 | 1.8 | 2604 | 2.03
2100 | 2000 | 1537 | 0.44 | 1631 | 0.53 | 1724 | 0.63 | 1810 | 0.73 | 1960 | 0.93 | 2097 | 1.14 | 2224 | 1.34 | 2344 | 1.56 | 2459 | 1.78 | 2570 | 2.02 | 2676 | 2.26
2310 | 2200 | 1672 | 0.56 | 1758 | 0.66 | 1844 | 0.77 | 1927 | 0.88 | 2073 | 1.1 | 2203 | 1.32 | 2325 | 1.55 | 2441 | 1.78 | 2550 | 2.01 | 2657 | 2.26 | 2759 | 2.51
2520 | 2400 | 1809 | 0.71 | 1888 | 0.82 | 1967 | 0.93 | 2045 | 1.05 | 2188 | 1.29 | 2314 | 1.53 | 2431 | 1.78 | 2542 | 2.02 | 2648 | 2.27 | 2750 | 2.53 | 2848 | 2.79
2730 | 2600 | 1946 | 0.88 | 2020 | 1 | 2093 | 1.12 | 2165 | 1.24 | 2304 | 1.51 | 2428 | 1.77 | 2540 | 2.03 | 2647 | 2.29 | 2750 | 2.56 | 2848 | 2.83 | 2943 | 3.11
2940 | 2800 | 2085 | 1.09 | 2154 | 1.21 | 2221 | 1.33 | 2289 | 1.47 | 2422 | 1.75 | 2543 | 2.03 | 2653 | 2.31 | 2756 | 2.59 | 2855 | 2.88 | 2950 | 3.16 | 3042 | 3.45
3150 | 3000 | 2224 | 1.32 | 2289 | 1.45 | 2352 | 1.58 | 2415 | 1.72 | 2541 | 2.02 | 2660 | 2.32 | 2768 | 2.62 | 2868 | 2.92 | 2963 | 3.22 | 3056 | 3.53 | 3145 | 3.84
3360 | 3200 | 2364 | 1.58 | 2425 | 1.72 | 2485 | 1.86 | 2544 | 2 | 2662 | 2.31 | 2777 | 2.64 | 2884 | 2.96 | 2982 | 3.28 | 3075 | 3.6 | 3164 | 3.92 | 3251 | 4.25
3570 | 3400 | 2505 | 1.88 | 2562 | 2.02 | 2618 | 2.17 | 2674 | 2.32 | 2785 | 2.64 | 2895 | 2.98 | 3000 | 3.33 | 3098 | 3.68 | 3189 | 4.01 | 3276 | 4.35 | 3359 | 4.69
Low-pressure range
CFM | OV | 5" SP |  | 5.5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP |  | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2100 | 2000 | 2780 | 2.5 | 2882 | 2.76 | 2982 | 3.03 | 3178 | 3.58
2310 | 2200 | 2858 | 2.77 | 2954 | 3.03 | 3048 | 3.3 | 3233 | 3.87 | 3413 | 4.48
2520 | 2400 | 2944 | 3.06 | 3036 | 3.33 | 3126 | 3.62 | 3301 | 4.2 | 3472 | 4.82 | 3639 | 5.47 | 3801 | 6.14
2730 | 2600 | 3035 | 3.39 | 3124 | 3.67 | 3212 | 3.97 | 3380 | 4.57 | 3542 | 5.21 | 3700 | 5.87 | 3856 | 6.56 | 4008 | 7.27 | 4157 | 8
2940 | 2800 | 3131 | 3.75 | 3217 | 4.04 | 3302 | 4.35 | 3466 | 4.98 | 3622 | 5.64 | 3773 | 6.31 | 3921 | 7.01 | 4066 | 7.74 | 4210 | 8.49 | 4350 | 9.26 | 4488 | 10.06
3150 | 3000 | 3231 | 4.14 | 3315 | 4.46 | 3397 | 4.78 | 3555 | 5.42 | 3708 | 6.1 | 3854 | 6.8 | 3996 | 7.52 | 4135 | 8.26 | 4272 | 9.03 | 4407 | 9.82 | 4540 | 10.63
3360 | 3200 | 3335 | 4.58 | 3417 | 4.91 | 3496 | 5.24 | 3649 | 5.91 | 3797 | 6.61 | 3941 | 7.33 | 4079 | 8.07 | 4213 | 8.83 | 4344 | 9.61 | 4473 | 10.42
3570 | 3400 | 3441 | 5.04 | 3521 | 5.39 | 3598 | 5.74 | 3748 | 6.44 | 3891 | 7.16 | 4030 | 7.9 | 4166 | 8.67 | 4297 | 9.46 | 4424 | 10.26 | 4548 | 11.07
3780 | 3600 | 3550 | 5.54 | 3627 | 5.9 | 3703 | 6.27 | 3849 | 7.01 | 3989 | 7.76 | 4124 | 8.53 | 4256 | 9.31 | 4384 | 10.12 | 4509 | 10.95
3990 | 3800 | 3661 | 6.08 | 3737 | 6.46 | 3810 | 6.84 | 3953 | 7.62 | 4090 | 8.41 | 4222 | 9.2 | 4350 | 10.01 | 4475 | 10.83 | 4597 | 11.68
4200 | 4000 | 3775 | 6.66 | 3848 | 7.06 | 3920 | 7.46 | 4059 | 8.27 | 4193 | 9.09 | 4323 | 9.92 | 4448 | 10.76 | 4569 | 11.6
4410 | 4200 | 3890 | 7.28 | 3962 | 7.7 | 4032 | 8.12 | 4168 | 8.96 | 4299 | 9.82 | 4426 | 10.68 | 4548 | 11.55
High-pressure range
1500CEB
Outlet Area 1.29 ft² ¦ Wheel Dia. 15.00 in ¦ Tip Speed 3.93 × RPM (ft/min) ¦ Max BHP = 0.211 × (RPM/1000)³ ¦ FEG75
MAXIMUM RPM: Class I — 2587 Class II — 3364 Class III — 4253 Class IV — 4580 (Selections above 4000 RPM not recommended — consult factory)
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1032 | 800 | 853 | 0.13 | 1091 | 0.25
1161 | 900 | 896 | 0.15 | 1119 | 0.28
1290 | 1000 | 941 | 0.17 | 1154 | 0.31 | 1341 | 0.47
1548 | 1200 | 1038 | 0.23 | 1235 | 0.39 | 1405 | 0.56 | 1561 | 0.74
1806 | 1400 | 1141 | 0.31 | 1325 | 0.49 | 1483 | 0.67 | 1627 | 0.86 | 1893 | 1.31
2064 | 1600 | 1245 | 0.4 | 1420 | 0.6 | 1570 | 0.8 | 1706 | 1.01 | 1952 | 1.48 | 2181 | 1.99
2322 | 1800 | 1352 | 0.51 | 1521 | 0.74 | 1662 | 0.96 | 1791 | 1.19 | 2026 | 1.68 | 2238 | 2.21 | 2441 | 2.8
2580 | 2000 | 1462 | 0.65 | 1624 | 0.9 | 1759 | 1.14 | 1882 | 1.39 | 2106 | 1.91 | 2309 | 2.47 | 2499 | 3.08 | 2682 | 3.72 | 2858 | 4.41
2838 | 2200 | 1576 | 0.81 | 1728 | 1.08 | 1860 | 1.35 | 1978 | 1.62 | 2192 | 2.18 | 2387 | 2.77 | 2568 | 3.4 | 2740 | 4.06 | 2907 | 4.76 | 3070 | 5.51
3096 | 2400 | 1692 | 1 | 1834 | 1.28 | 1963 | 1.58 | 2077 | 1.88 | 2283 | 2.48 | 2470 | 3.1 | 2645 | 3.76 | 2809 | 4.44 | 2967 | 5.17 | 3121 | 5.93 | 3272 | 6.72
3354 | 2600 | 1811 | 1.22 | 1942 | 1.52 | 2067 | 1.85 | 2178 | 2.17 | 2376 | 2.81 | 2557 | 3.47 | 2726 | 4.15 | 2886 | 4.87 | 3037 | 5.62 | 3183 | 6.39 | 3326 | 7.21
3612 | 2800 | 1930 | 1.47 | 2052 | 1.79 | 2172 | 2.14 | 2282 | 2.49 | 2474 | 3.18 | 2649 | 3.88 | 2812 | 4.6 | 2966 | 5.34 | 3114 | 6.12 | 3255 | 6.92 | 3391 | 7.75
3870 | 3000 | 2051 | 1.76 | 2165 | 2.1 | 2279 | 2.46 | 2386 | 2.84 | 2574 | 3.58 | 2743 | 4.32 | 2902 | 5.08 | 3051 | 5.86 | 3194 | 6.66 | 3331 | 7.49 | 3463 | 8.35
4386 | 3400 | 2295 | 2.46 | 2397 | 2.83 | 2497 | 3.22 | 2597 | 3.65 | 2779 | 4.49 | 2940 | 5.33 | 3089 | 6.17 | 3231 | 7.03 | 3366 | 7.9 | 3495 | 8.78 | 3621 | 9.7
4902 | 3800 | 2543 | 3.34 | 2634 | 3.74 | 2724 | 4.17 | 2814 | 4.62 | 2988 | 5.57 | 3144 | 6.51 | 3286 | 7.44 | 3420 | 8.38 | 3549 | 9.34 | 3673 | 10.31 | 3792 | 11.28
5418 | 4200 | 2792 | 4.41 | 2875 | 4.85 | 2957 | 5.31 | 3038 | 5.79 | 3200 | 6.82 | 3352 | 7.87 | 3490 | 8.91 | 3618 | 9.93 | 3741 | 10.98 | 3859 | 12.03 | 3974 | 13.09
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3096 | 2400 | 3419 | 7.55
3354 | 2600 | 3467 | 8.06 | 3604 | 8.93 | 3739 | 9.84
3612 | 2800 | 3524 | 8.61 | 3656 | 9.51 | 3785 | 10.44 | 3912 | 11.39 | 4036 | 12.37
3870 | 3000 | 3591 | 9.23 | 3717 | 10.15 | 3840 | 11.09 | 3962 | 12.06 | 4082 | 13.06 | 4200 | 14.09 | 4317 | 15.15
4128 | 3200 | 3665 | 9.91 | 3786 | 10.85 | 3904 | 11.81 | 4021 | 12.8 | 4136 | 13.82 | 4250 | 14.86 | 4362 | 15.93 | 4473 | 17.03 | 4582 | 18.15
4386 | 3400 | 3743 | 10.64 | 3861 | 11.61 | 3975 | 12.59 | 4088 | 13.61 | 4198 | 14.64 | 4307 | 15.7 | 4416 | 16.79 | 4523 | 17.91
4644 | 3600 | 3823 | 11.42 | 3939 | 12.42 | 4051 | 13.43 | 4160 | 14.47 | 4267 | 15.52 | 4373 | 16.61 | 4477 | 17.72 | 4580 | 18.85
4902 | 3800 | 3907 | 12.27 | 4020 | 13.29 | 4130 | 14.34 | 4237 | 15.4 | 4342 | 16.49 | 4444 | 17.59 | 4545 | 18.72
5160 | 4000 | 3994 | 13.18 | 4104 | 14.23 | 4211 | 15.29 | 4316 | 16.39 | 4419 | 17.5 | 4520 | 18.65
5418 | 4200 | 4084 | 14.15 | 4191 | 15.23 | 4296 | 16.33 | 4398 | 17.44 | 4499 | 18.59 | 4598 | 19.75
5934 | 4600 | 4269 | 16.26 | 4373 | 17.43 | 4473 | 18.6 | 4572 | 19.79
6450 | 5000 | 4461 | 18.61 | 4561 | 19.87
High-pressure range
1650CEB
Outlet Area 1.57 ft² ¦ Wheel Dia. 16.50 in ¦ Tip Speed 4.32 × RPM (ft/min) ¦ Max BHP = 0.339 × (RPM/1000)³ ¦ FEG75
MAXIMUM RPM: Class I — 2352 Class II — 3058 Class III — 3867 Class IV — 4167 (Selections above 4000 RPM not recommended — consult factory)
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1256 | 800 | 777 | 0.15 | 992 | 0.3
1413 | 900 | 816 | 0.18 | 1019 | 0.34
1570 | 1000 | 858 | 0.21 | 1051 | 0.38 | 1220 | 0.57
1884 | 1200 | 947 | 0.29 | 1125 | 0.47 | 1279 | 0.68 | 1421 | 0.9
2198 | 1400 | 1041 | 0.38 | 1208 | 0.59 | 1351 | 0.81 | 1482 | 1.05 | 1722 | 1.59
2512 | 1600 | 1137 | 0.49 | 1295 | 0.73 | 1431 | 0.98 | 1554 | 1.24 | 1778 | 1.8 | 1985 | 2.42
2826 | 1800 | 1234 | 0.63 | 1387 | 0.9 | 1516 | 1.17 | 1633 | 1.45 | 1845 | 2.05 | 2038 | 2.7 | 2222 | 3.4
3140 | 2000 | 1335 | 0.79 | 1482 | 1.1 | 1604 | 1.39 | 1716 | 1.7 | 1919 | 2.33 | 2103 | 3.01 | 2275 | 3.74 | 2441 | 4.53 | 2601 | 5.36
3454 | 2200 | 1440 | 0.99 | 1577 | 1.32 | 1697 | 1.65 | 1803 | 1.98 | 1998 | 2.66 | 2174 | 3.37 | 2339 | 4.14 | 2495 | 4.94 | 2646 | 5.8 | 2793 | 6.69
3768 | 2400 | 1546 | 1.22 | 1674 | 1.57 | 1791 | 1.94 | 1894 | 2.29 | 2081 | 3.03 | 2250 | 3.78 | 2409 | 4.57 | 2559 | 5.41 | 2702 | 6.29 | 2841 | 7.21 | 2977 | 8.17
4082 | 2600 | 1654 | 1.49 | 1773 | 1.86 | 1887 | 2.26 | 1987 | 2.65 | 2167 | 3.43 | 2331 | 4.23 | 2484 | 5.06 | 2629 | 5.93 | 2766 | 6.84 | 2899 | 7.79 | 3028 | 8.77
4396 | 2800 | 1764 | 1.81 | 1874 | 2.19 | 1983 | 2.62 | 2082 | 3.04 | 2256 | 3.88 | 2415 | 4.73 | 2563 | 5.61 | 2702 | 6.5 | 2836 | 7.45 | 2964 | 8.42 | 3088 | 9.44
4710 | 3000 | 1874 | 2.16 | 1977 | 2.57 | 2080 | 3.01 | 2177 | 3.47 | 2348 | 4.37 | 2501 | 5.28 | 2645 | 6.2 | 2780 | 7.14 | 2910 | 8.12 | 3035 | 9.13 | 3154 | 10.16
5338 | 3400 | 2098 | 3.03 | 2190 | 3.48 | 2280 | 3.95 | 2370 | 4.46 | 2536 | 5.5 | 2682 | 6.52 | 2817 | 7.54 | 2945 | 8.58 | 3068 | 9.64 | 3185 | 10.71 | 3299 | 11.82
5966 | 3800 | 2324 | 4.11 | 2407 | 4.6 | 2488 | 5.11 | 2569 | 5.66 | 2727 | 6.82 | 2869 | 7.97 | 2997 | 9.09 | 3119 | 10.24 | 3236 | 11.41 | 3348 | 12.58 | 3456 | 13.76
6594 | 4200 | 2552 | 5.43 | 2627 | 5.96 | 2701 | 6.52 | 2774 | 7.1 | 2921 | 8.35 | 3059 | 9.64 | 3184 | 10.89 | 3301 | 12.15 | 3412 | 13.41 | 3519 | 14.69 | 3623 | 15.98
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3768 | 2400 | 3111 | 9.18
4082 | 2600 | 3155 | 9.8 | 3280 | 10.86 | 3402 | 11.96
4396 | 2800 | 3209 | 10.49 | 3328 | 11.57 | 3445 | 12.7 | 3560 | 13.85 | 3673 | 15.04
4710 | 3000 | 3271 | 11.25 | 3384 | 12.35 | 3496 | 13.5 | 3606 | 14.67 | 3715 | 15.89 | 3822 | 17.13 | 3928 | 18.41
5024 | 3200 | 3338 | 12.07 | 3448 | 13.21 | 3555 | 14.37 | 3661 | 15.58 | 3765 | 16.81 | 3868 | 18.07 | 3970 | 19.37 | 4070 | 20.7 | 4169 | 22.05
5338 | 3400 | 3410 | 12.97 | 3516 | 14.13 | 3621 | 15.34 | 3722 | 16.55 | 3823 | 17.82 | 3921 | 19.1 | 4019 | 20.42 | 4116 | 21.77 | 4212 | 23.15 | 4307 | 24.56 | 4400 | 25.99
5652 | 3600 | 3483 | 13.92 | 3588 | 15.13 | 3690 | 16.36 | 3789 | 17.62 | 3886 | 18.9 | 3982 | 20.22 | 4076 | 21.56 | 4169 | 22.93 | 4262 | 24.34 | 4353 | 25.76 | 4444 | 27.22
5966 | 3800 | 3560 | 14.96 | 3662 | 16.19 | 3762 | 17.46 | 3860 | 18.77 | 3955 | 20.09 | 4047 | 21.41 | 4139 | 22.79 | 4229 | 24.19 | 4318 | 25.61 | 4406 | 27.06 | 4493 | 28.52
6280 | 4000 | 3640 | 16.08 | 3740 | 17.35 | 3837 | 18.65 | 3933 | 19.98 | 4026 | 21.33 | 4117 | 22.71 | 4206 | 24.11 | 4294 | 25.54 | 4380 | 26.98 | 4465 | 28.44 | 4550 | 29.95
6594 | 4200 | 3723 | 17.28 | 3820 | 18.59 | 3915 | 19.92 | 4008 | 21.27 | 4099 | 22.65 | 4189 | 24.07 | 4276 | 25.5 | 4362 | 26.96 | 4446 | 28.43 | 4529 | 29.93
7222 | 4600 | 3893 | 19.87 | 3987 | 21.29 | 4078 | 22.71 | 4167 | 24.14 | 4254 | 25.59 | 4339 | 27.05 | 4424 | 28.57 | 4507 | 30.09 | 4588 | 31.63
7850 | 5000 | 4069 | 22.75 | 4159 | 24.26 | 4247 | 25.79 | 4334 | 27.34 | 4418 | 28.89 | 4500 | 30.44 | 4581 | 32.01
8160 | 5197 | 4158 | 24.28 | 4246 | 25.84 | 4333 | 27.43 | 4418 | 29.03 | 4501 | 30.63 | 4582 | 32.24
High-pressure range
1825CEB
Outlet Area 1.92 ft² ¦ Wheel Dia. 18.25 in ¦ Tip Speed 4.78 × RPM (ft/min) ¦ Max BHP = 0.552 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 2118 Class II — 2729 Class III — 3473 Class IV — 3766
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1536 | 800 | 695 | 0.17
1728 | 900 | 724 | 0.2 | 932 | 0.38
1920 | 1000 | 757 | 0.24 | 951 | 0.42 | 1126 | 0.64
2304 | 1200 | 831 | 0.32 | 1002 | 0.53 | 1160 | 0.76 | 1306 | 1.02
2688 | 1400 | 914 | 0.42 | 1066 | 0.66 | 1208 | 0.91 | 1342 | 1.19
3072 | 1600 | 1003 | 0.55 | 1138 | 0.81 | 1267 | 1.09 | 1391 | 1.39 | 1621 | 2.03
3456 | 1800 | 1096 | 0.71 | 1217 | 1 | 1335 | 1.3 | 1449 | 1.62 | 1663 | 2.3 | 1864 | 3.06
3840 | 2000 | 1191 | 0.91 | 1302 | 1.22 | 1409 | 1.55 | 1514 | 1.88 | 1714 | 2.61 | 1903 | 3.4 | 2081 | 4.24 | 2252 | 5.15
4224 | 2200 | 1288 | 1.13 | 1391 | 1.48 | 1489 | 1.83 | 1586 | 2.2 | 1773 | 2.96 | 1950 | 3.78 | 2120 | 4.67 | 2282 | 5.6 | 2437 | 6.58
4608 | 2400 | 1387 | 1.4 | 1482 | 1.78 | 1573 | 2.16 | 1663 | 2.55 | 1838 | 3.36 | 2005 | 4.22 | 2165 | 5.13 | 2320 | 6.11 | 2469 | 7.13 | 2612 | 8.18
4992 | 2600 | 1487 | 1.71 | 1576 | 2.12 | 1661 | 2.53 | 1744 | 2.94 | 1908 | 3.81 | 2066 | 4.71 | 2218 | 5.66 | 2365 | 6.67 | 2507 | 7.72 | 2645 | 8.81 | 2779 | 9.95
5376 | 2800 | 1588 | 2.07 | 1671 | 2.5 | 1751 | 2.94 | 1829 | 3.39 | 1982 | 4.3 | 2132 | 5.25 | 2276 | 6.25 | 2416 | 7.28 | 2553 | 8.38 | 2685 | 9.51 | 2814 | 10.68
5760 | 3000 | 1689 | 2.47 | 1768 | 2.94 | 1843 | 3.41 | 1917 | 3.88 | 2061 | 4.86 | 2202 | 5.85 | 2340 | 6.89 | 2473 | 7.97 | 2604 | 9.09 | 2730 | 10.25 | 2854 | 11.46
6528 | 3400 | 1895 | 3.46 | 1964 | 3.98 | 2032 | 4.5 | 2099 | 5.04 | 2227 | 6.12 | 2354 | 7.23 | 2479 | 8.36 | 2601 | 9.53 | 2720 | 10.73 | 2837 | 11.97 | 2952 | 13.25
7296 | 3800 | 2102 | 4.68 | 2165 | 5.26 | 2226 | 5.85 | 2287 | 6.45 | 2404 | 7.64 | 2518 | 8.85 | 2631 | 10.09 | 2743 | 11.35 | 2853 | 12.64 | 2961 | 13.97 | 3067 | 15.33
8064 | 4200 | 2310 | 6.17 | 2368 | 6.82 | 2424 | 7.47 | 2479 | 8.12 | 2587 | 9.43 | 2692 | 10.76 | 2795 | 12.11 | 2897 | 13.48 | 2999 | 14.87 | 3099 | 16.28 | 3197 | 17.71
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
4992 | 2600 | 2909 | 11.13
5376 | 2800 | 2939 | 11.89 | 3061 | 13.14
5760 | 3000 | 2975 | 12.71 | 3093 | 13.99 | 3208 | 15.31 | 3321 | 16.66
6144 | 3200 | 3017 | 13.6 | 3131 | 14.92 | 3243 | 16.28 | 3352 | 17.66 | 3459 | 19.08 | 3565 | 20.54
6528 | 3400 | 3064 | 14.56 | 3174 | 15.91 | 3282 | 17.3 | 3388 | 18.72 | 3492 | 20.17 | 3594 | 21.66 | 3695 | 23.19 | 3794 | 24.74
6912 | 3600 | 3116 | 15.6 | 3222 | 16.99 | 3326 | 18.4 | 3429 | 19.87 | 3530 | 21.35 | 3630 | 22.89 | 3727 | 24.42 | 3823 | 26 | 3918 | 27.62 | 4012 | 29.27
7296 | 3800 | 3172 | 16.72 | 3274 | 18.13 | 3375 | 19.59 | 3475 | 21.1 | 3573 | 22.62 | 3669 | 24.17 | 3764 | 25.75 | 3858 | 27.38 | 3950 | 29.01 | 4041 | 30.69 | 4131 | 32.4
7680 | 4000 | 3231 | 17.91 | 3331 | 19.39 | 3428 | 20.86 | 3525 | 22.4 | 3620 | 23.97 | 3713 | 25.55 | 3806 | 27.18 | 3897 | 28.83 | 3987 | 30.51 | 4075 | 32.2 | 4163 | 33.94
8064 | 4200 | 3295 | 19.21 | 3391 | 20.71 | 3485 | 22.23 | 3579 | 23.81 | 3671 | 25.4 | 3761 | 27.01 | 3851 | 28.67 | 3940 | 30.37 | 4027 | 32.07 | 4114 | 33.82 | 4199 | 35.58
8832 | 4600 | 3431 | 22.03 | 3520 | 23.61 | 3609 | 25.24 | 3696 | 26.87 | 3783 | 28.55 | 3869 | 30.25 | 3954 | 31.98 | 4037 | 33.71 | 4120 | 35.5 | 4202 | 37.32 | 4283 | 39.15
9600 | 5000 | 3577 | 25.23 | 3661 | 26.9 | 3744 | 28.59 | 3827 | 30.34 | 3908 | 32.09 | 3989 | 33.87 | 4069 | 35.67 | 4148 | 37.49 | 4227 | 39.36 | 4305 | 41.24 | 4382 | 43.14
High-pressure range
2000CEB
Outlet Area 2.30 ft² ¦ Wheel Dia. 20.00 in ¦ Tip Speed 5.24 × RPM (ft/min) ¦ Max BHP = 0.872 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 1932 Class II — 2490 Class III — 3169 Class IV — 3442
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1840 | 800 | 634 | 0.21
2070 | 900 | 660 | 0.24 | 850 | 0.46
2300 | 1000 | 690 | 0.28 | 868 | 0.51 | 1027 | 0.77
2760 | 1200 | 758 | 0.38 | 914 | 0.63 | 1058 | 0.91 | 1191 | 1.22
3220 | 1400 | 833 | 0.51 | 971 | 0.78 | 1102 | 1.09 | 1224 | 1.42
3680 | 1600 | 914 | 0.66 | 1037 | 0.97 | 1155 | 1.3 | 1268 | 1.66 | 1479 | 2.44
4140 | 1800 | 998 | 0.85 | 1109 | 1.2 | 1217 | 1.56 | 1321 | 1.94 | 1517 | 2.76 | 1700 | 3.66
4600 | 2000 | 1085 | 1.08 | 1186 | 1.46 | 1284 | 1.85 | 1380 | 2.25 | 1563 | 3.12 | 1735 | 4.07 | 1899 | 5.09 | 2054 | 6.17
5060 | 2200 | 1173 | 1.35 | 1267 | 1.77 | 1357 | 2.19 | 1445 | 2.62 | 1616 | 3.54 | 1778 | 4.53 | 1933 | 5.59 | 2081 | 6.71 | 2223 | 7.89
5520 | 2400 | 1263 | 1.67 | 1350 | 2.12 | 1433 | 2.58 | 1515 | 3.05 | 1675 | 4.02 | 1828 | 5.05 | 1975 | 6.15 | 2116 | 7.32 | 2252 | 8.54 | 2383 | 9.81
5980 | 2600 | 1354 | 2.04 | 1435 | 2.53 | 1513 | 3.02 | 1589 | 3.52 | 1739 | 4.55 | 1883 | 5.64 | 2022 | 6.78 | 2157 | 7.99 | 2287 | 9.25 | 2413 | 10.56 | 2535 | 11.93
6440 | 2800 | 1446 | 2.47 | 1522 | 2.99 | 1595 | 3.52 | 1666 | 4.05 | 1806 | 5.14 | 1943 | 6.28 | 2075 | 7.48 | 2203 | 8.72 | 2328 | 10.03 | 2449 | 11.39 | 2566 | 12.79
6900 | 3000 | 1538 | 2.95 | 1610 | 3.51 | 1679 | 4.07 | 1746 | 4.64 | 1878 | 5.81 | 2007 | 7 | 2133 | 8.25 | 2255 | 9.54 | 2374 | 10.88 | 2490 | 12.28 | 2603 | 13.73
7820 | 3400 | 1725 | 4.12 | 1789 | 4.75 | 1851 | 5.38 | 1911 | 6.02 | 2029 | 7.31 | 2145 | 8.65 | 2259 | 10 | 2371 | 11.4 | 2480 | 12.84 | 2587 | 14.33 | 2691 | 15.85
8740 | 3800 | 1913 | 5.58 | 1971 | 6.28 | 2027 | 6.98 | 2082 | 7.69 | 2189 | 9.12 | 2294 | 10.58 | 2398 | 12.08 | 2500 | 13.58 | 2600 | 15.12 | 2699 | 16.72 | 2796 | 18.34
9660 | 4200 | 2103 | 7.36 | 2155 | 8.13 | 2207 | 8.91 | 2257 | 9.68 | 2356 | 11.26 | 2452 | 12.86 | 2546 | 14.47 | 2640 | 16.12 | 2733 | 17.79 | 2824 | 19.47 | 2914 | 21.19
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
5980 | 2600 | 2654 | 13.35
6440 | 2800 | 2681 | 14.25 | 2792 | 15.74
6900 | 3000 | 2713 | 15.22 | 2821 | 16.76 | 2926 | 18.34 | 3030 | 19.98
7360 | 3200 | 2751 | 16.28 | 2856 | 17.88 | 2958 | 19.5 | 3057 | 21.15 | 3155 | 22.85 | 3252 | 24.61
7820 | 3400 | 2794 | 17.44 | 2894 | 19.05 | 2993 | 20.72 | 3090 | 22.43 | 3185 | 24.17 | 3279 | 25.97 | 3370 | 27.77 | 3461 | 29.64
8280 | 3600 | 2841 | 18.68 | 2938 | 20.34 | 3033 | 22.04 | 3127 | 23.79 | 3220 | 25.59 | 3310 | 27.4 | 3400 | 29.28 | 3487 | 31.15 | 3574 | 33.1 | 3660 | 35.08
8740 | 3800 | 2892 | 20.02 | 2985 | 21.71 | 3078 | 23.47 | 3169 | 25.27 | 3258 | 27.08 | 3346 | 28.94 | 3433 | 30.85 | 3519 | 32.8 | 3603 | 34.76 | 3686 | 36.77 | 3768 | 38.81
9200 | 4000 | 2946 | 21.45 | 3036 | 23.18 | 3126 | 24.99 | 3214 | 26.82 | 3301 | 28.7 | 3386 | 30.59 | 3471 | 32.56 | 3554 | 34.53 | 3636 | 36.54 | 3717 | 38.58 | 3797 | 40.66
9660 | 4200 | 3003 | 22.97 | 3091 | 24.78 | 3177 | 26.61 | 3263 | 28.5 | 3347 | 30.4 | 3430 | 32.35 | 3512 | 34.34 | 3593 | 36.37 | 3673 | 38.42 | 3752 | 40.51 | 3830 | 42.63
10580 | 4600 | 3127 | 26.35 | 3209 | 28.26 | 3290 | 30.21 | 3370 | 32.17 | 3449 | 34.17 | 3527 | 36.19 | 3605 | 38.28 | 3681 | 40.36 | 3757 | 42.51 | 3832 | 44.69 | 3906 | 46.89
11500 | 5000 | 3259 | 30.15 | 3336 | 32.16 | 3412 | 34.19 | 3488 | 36.29 | 3562 | 38.38 | 3636 | 40.52 | 3710 | 42.71 | 3782 | 44.89 | 3854 | 47.11 | 3925 | 49.36 | 3995 | 51.63
High-pressure range
2225CEB
Outlet Area 2.85 ft² ¦ Wheel Dia. 22.25 in ¦ Tip Speed 5.83 × RPM (ft/min) ¦ Max BHP = 1.49 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 1737 Class II — 2238 Class III — 2848 Class IV — 3088
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2280 | 800 | 570 | 0.26
2565 | 900 | 594 | 0.3 | 764 | 0.57
2850 | 1000 | 621 | 0.35 | 780 | 0.63 | 923 | 0.95
3420 | 1200 | 681 | 0.47 | 822 | 0.78 | 951 | 1.13 | 1071 | 1.52
3990 | 1400 | 749 | 0.63 | 874 | 0.97 | 991 | 1.35 | 1101 | 1.76
4560 | 1600 | 822 | 0.82 | 933 | 1.21 | 1039 | 1.62 | 1140 | 2.05 | 1330 | 3.02
5130 | 1800 | 898 | 1.06 | 998 | 1.49 | 1094 | 1.93 | 1188 | 2.4 | 1364 | 3.42 | 1528 | 4.53
5700 | 2000 | 976 | 1.34 | 1067 | 1.81 | 1155 | 2.29 | 1241 | 2.79 | 1405 | 3.87 | 1560 | 5.04 | 1707 | 6.3 | 1847 | 7.64
6270 | 2200 | 1055 | 1.68 | 1139 | 2.19 | 1220 | 2.71 | 1300 | 3.26 | 1453 | 4.39 | 1599 | 5.61 | 1738 | 6.92 | 1871 | 8.31 | 1999 | 9.78
6840 | 2400 | 1136 | 2.07 | 1214 | 2.63 | 1289 | 3.2 | 1363 | 3.78 | 1506 | 4.98 | 1644 | 6.27 | 1775 | 7.62 | 1902 | 9.06 | 2024 | 10.57 | 2142 | 12.15
7410 | 2600 | 1218 | 2.53 | 1291 | 3.13 | 1361 | 3.74 | 1429 | 4.36 | 1564 | 5.64 | 1693 | 6.98 | 1818 | 8.4 | 1939 | 9.89 | 2056 | 11.46 | 2169 | 13.08 | 2279 | 14.78
7980 | 2800 | 1301 | 3.06 | 1369 | 3.71 | 1435 | 4.36 | 1499 | 5.02 | 1625 | 6.38 | 1747 | 7.78 | 1866 | 9.27 | 1981 | 10.81 | 2093 | 12.43 | 2202 | 14.12 | 2307 | 15.84
8550 | 3000 | 1384 | 3.67 | 1448 | 4.35 | 1510 | 5.05 | 1571 | 5.76 | 1689 | 7.2 | 1805 | 8.68 | 1918 | 10.22 | 2028 | 11.83 | 2135 | 13.5 | 2239 | 15.23 | 2340 | 17.01
9690 | 3400 | 1552 | 5.11 | 1609 | 5.89 | 1665 | 6.68 | 1720 | 7.47 | 1825 | 9.07 | 1929 | 10.72 | 2032 | 12.4 | 2132 | 14.13 | 2230 | 15.92 | 2326 | 17.76 | 2420 | 19.65
10830 | 3800 | 1722 | 6.93 | 1773 | 7.79 | 1824 | 8.67 | 1874 | 9.55 | 1970 | 11.33 | 2064 | 13.14 | 2157 | 14.98 | 2248 | 16.83 | 2339 | 18.76 | 2427 | 20.72 | 2514 | 22.73
11970 | 4200 | 1893 | 9.15 | 1940 | 10.1 | 1986 | 11.06 | 2031 | 12.02 | 2120 | 13.98 | 2206 | 15.96 | 2290 | 17.95 | 2375 | 20.01 | 2458 | 22.06 | 2540 | 24.14 | 2621 | 26.29
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
7410 | 2600 | 2386 | 16.54
7980 | 2800 | 2410 | 17.65 | 2510 | 19.5
8550 | 3000 | 2440 | 18.87 | 2536 | 20.76 | 2631 | 22.73 | 2724 | 24.75
9120 | 3200 | 2474 | 20.19 | 2567 | 22.13 | 2659 | 24.15 | 2749 | 26.22 | 2837 | 28.33 | 2923 | 30.48
9690 | 3400 | 2512 | 21.6 | 2603 | 23.63 | 2691 | 25.67 | 2778 | 27.78 | 2864 | 29.96 | 2948 | 32.18 | 3030 | 34.42 | 3112 | 36.74
10260 | 3600 | 2554 | 23.13 | 2642 | 25.21 | 2727 | 27.31 | 2812 | 29.5 | 2895 | 31.71 | 2976 | 33.95 | 3057 | 36.28 | 3135 | 38.6 | 3213 | 41 | 3290 | 43.45
10830 | 3800 | 2600 | 24.8 | 2685 | 26.93 | 2767 | 29.07 | 2849 | 31.3 | 2929 | 33.55 | 3009 | 35.89 | 3087 | 38.24 | 3164 | 40.65 | 3239 | 43.06 | 3314 | 45.56 | 3388 | 48.11
11400 | 4000 | 2649 | 26.58 | 2731 | 28.77 | 2811 | 30.97 | 2890 | 33.24 | 2968 | 35.56 | 3045 | 37.93 | 3120 | 40.31 | 3195 | 42.77 | 3269 | 45.27 | 3342 | 47.81 | 3414 | 50.4
11970 | 4200 | 2701 | 28.49 | 2780 | 30.73 | 2857 | 32.98 | 2934 | 35.31 | 3009 | 37.66 | 3084 | 40.09 | 3158 | 42.57 | 3230 | 45.04 | 3302 | 47.6 | 3373 | 50.18 | 3443 | 52.8
13110 | 4600 | 2812 | 32.66 | 2886 | 35.04 | 2958 | 37.42 | 3030 | 39.86 | 3102 | 42.38 | 3172 | 44.88 | 3241 | 47.42 | 3310 | 50.03 | 3378 | 52.68 | 3445 | 55.36 | 3512 | 58.11
14250 | 5000 | 2932 | 37.42 | 3001 | 39.9 | 3069 | 42.41 | 3137 | 45 | 3204 | 47.61 | 3270 | 50.24 | 3336 | 52.94 | 3401 | 55.64 | 3466 | 58.42 | 3529 | 61.16 | 3593 | 64.03
High-pressure range
2450CEB
Outlet Area 3.45 ft² ¦ Wheel Dia. 24.50 in ¦ Tip Speed 6.41 × RPM (ft/min) ¦ Max BHP = 2.40 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 1577 Class II — 2033 Class III — 2587 Class IV — 2808
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2760 | 800 | 517 | 0.31
3105 | 900 | 539 | 0.36 | 694 | 0.69
3450 | 1000 | 563 | 0.42 | 708 | 0.76 | 838 | 1.15
4140 | 1200 | 618 | 0.57 | 746 | 0.95 | 863 | 1.37 | 972 | 1.84
4830 | 1400 | 680 | 0.76 | 793 | 1.18 | 899 | 1.63 | 999 | 2.13
5520 | 1600 | 746 | 0.99 | 846 | 1.46 | 943 | 1.96 | 1035 | 2.49 | 1207 | 3.65
6210 | 1800 | 815 | 1.28 | 905 | 1.79 | 993 | 2.33 | 1078 | 2.9 | 1238 | 4.13 | 1388 | 5.49
6900 | 2000 | 885 | 1.62 | 968 | 2.19 | 1048 | 2.77 | 1126 | 3.38 | 1276 | 4.69 | 1416 | 6.1 | 1550 | 7.63 | 1677 | 9.25
7590 | 2200 | 957 | 2.03 | 1034 | 2.65 | 1107 | 3.28 | 1180 | 3.94 | 1319 | 5.32 | 1452 | 6.8 | 1578 | 8.38 | 1699 | 10.07 | 1815 | 11.84
8280 | 2400 | 1031 | 2.51 | 1101 | 3.17 | 1170 | 3.87 | 1237 | 4.57 | 1367 | 6.02 | 1492 | 7.58 | 1612 | 9.23 | 1727 | 10.97 | 1838 | 12.8 | 1945 | 14.71
8970 | 2600 | 1105 | 3.06 | 1171 | 3.79 | 1235 | 4.53 | 1297 | 5.28 | 1419 | 6.82 | 1537 | 8.46 | 1651 | 10.18 | 1760 | 11.97 | 1867 | 13.88 | 1969 | 15.83 | 2069 | 17.89
9660 | 2800 | 1180 | 3.7 | 1242 | 4.48 | 1301 | 5.26 | 1360 | 6.07 | 1474 | 7.71 | 1586 | 9.43 | 1694 | 11.22 | 1798 | 13.07 | 1900 | 15.04 | 1999 | 17.08 | 2095 | 19.19
10350 | 3000 | 1255 | 4.42 | 1313 | 5.25 | 1370 | 6.1 | 1425 | 6.96 | 1532 | 8.7 | 1638 | 10.49 | 1741 | 12.37 | 1840 | 14.3 | 1938 | 16.33 | 2032 | 18.41 | 2125 | 20.6
11730 | 3400 | 1408 | 6.18 | 1460 | 7.12 | 1510 | 8.06 | 1560 | 9.03 | 1656 | 10.97 | 1751 | 12.97 | 1844 | 15 | 1935 | 17.09 | 2024 | 19.26 | 2111 | 21.48 | 2197 | 23.79
13110 | 3800 | 1561 | 8.36 | 1608 | 9.41 | 1654 | 10.46 | 1699 | 11.53 | 1787 | 13.69 | 1872 | 15.87 | 1957 | 18.11 | 2040 | 20.36 | 2122 | 22.67 | 2203 | 25.07 | 2282 | 27.51
14490 | 4200 | 1716 | 11.03 | 1759 | 12.19 | 1801 | 13.36 | 1842 | 14.52 | 1923 | 16.9 | 2001 | 19.28 | 2078 | 21.71 | 2155 | 24.19 | 2230 | 26.66 | 2305 | 29.2 | 2379 | 31.81
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
8970 | 2600 | 2166 | 20.01
9660 | 2800 | 2188 | 21.36 | 2279 | 23.61
10350 | 3000 | 2215 | 22.84 | 2303 | 25.15 | 2389 | 27.53 | 2473 | 29.96
11040 | 3200 | 2246 | 24.44 | 2331 | 26.81 | 2414 | 29.23 | 2496 | 31.75 | 2576 | 34.31 | 2654 | 36.9
11730 | 3400 | 2280 | 26.13 | 2363 | 28.6 | 2443 | 31.08 | 2522 | 33.63 | 2600 | 36.26 | 2676 | 38.93 | 2751 | 41.67 | 2825 | 44.46
12420 | 3600 | 2319 | 28.01 | 2398 | 30.5 | 2476 | 33.07 | 2553 | 35.71 | 2628 | 38.37 | 2702 | 41.1 | 2775 | 43.9 | 2847 | 46.76 | 2917 | 49.63 | 2987 | 52.6
13110 | 3800 | 2360 | 30.01 | 2437 | 32.58 | 2512 | 35.19 | 2586 | 37.87 | 2659 | 40.61 | 2731 | 43.41 | 2802 | 46.27 | 2872 | 49.18 | 2941 | 52.15 | 3009 | 55.17 | 3076 | 58.24
13800 | 4000 | 2404 | 32.15 | 2478 | 34.77 | 2551 | 37.46 | 2623 | 40.21 | 2694 | 43.03 | 2764 | 45.9 | 2833 | 48.82 | 2901 | 51.79 | 2968 | 54.81 | 3034 | 57.87 | 3099 | 60.97
14490 | 4200 | 2451 | 34.45 | 2523 | 37.17 | 2593 | 39.9 | 2663 | 42.72 | 2732 | 45.6 | 2800 | 48.54 | 2866 | 51.48 | 2933 | 54.56 | 2998 | 57.63 | 3062 | 60.73 | 3126 | 63.93
15870 | 4600 | 2552 | 39.51 | 2619 | 42.37 | 2685 | 45.29 | 2750 | 48.22 | 2815 | 51.24 | 2879 | 54.29 | 2942 | 57.38 | 3005 | 60.57 | 3067 | 63.79 | 3128 | 67.05 | 3188 | 70.32
17250 | 5000 | 2660 | 45.23 | 2723 | 48.24 | 2785 | 51.29 | 2847 | 54.43 | 2908 | 57.61 | 2968 | 60.79 | 3028 | 64.05 | 3087 | 67.33 | 3146 | 70.68 | 3204 | 74.06 | 3261 | 77.46
High-pressure range
2700CEB
Outlet Area 4.19 ft² ¦ Wheel Dia. 27.00 in ¦ Tip Speed 7.08 × RPM (ft/min) ¦ Max BHP = 4.05 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 1397 Class II — 1803 Class III — 2287 Class IV — 2544
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3352 | 800 | 457 | 0.36 | 592 | 0.72
3771 | 900 | 480 | 0.43 | 603 | 0.79 | 725 | 1.27
4190 | 1000 | 504 | 0.5 | 621 | 0.89 | 726 | 1.33
5028 | 1200 | 557 | 0.69 | 661 | 1.11 | 755 | 1.59 | 843 | 2.12
5866 | 1400 | 614 | 0.91 | 709 | 1.4 | 795 | 1.92 | 875 | 2.48 | 1026 | 3.75
6704 | 1600 | 674 | 1.2 | 761 | 1.75 | 840 | 2.32 | 914 | 2.91 | 1051 | 4.21 | 1184 | 5.74
7542 | 1800 | 736 | 1.54 | 816 | 2.15 | 890 | 2.78 | 959 | 3.43 | 1088 | 4.82 | 1206 | 6.32 | 1324 | 8.05 | 1449 | 10.16
8380 | 2000 | 800 | 1.96 | 874 | 2.63 | 943 | 3.33 | 1007 | 4.02 | 1128 | 5.49 | 1241 | 7.08 | 1346 | 8.77 | 1452 | 10.68 | 1564 | 12.93
9218 | 2200 | 865 | 2.45 | 934 | 3.19 | 998 | 3.94 | 1059 | 4.7 | 1174 | 6.3 | 1280 | 7.95 | 1381 | 9.72 | 1476 | 11.58 | 1572 | 13.64 | 1672 | 15.99
10056 | 2400 | 932 | 3.04 | 995 | 3.83 | 1056 | 4.65 | 1113 | 5.47 | 1222 | 7.17 | 1323 | 8.93 | 1419 | 10.77 | 1511 | 12.72 | 1598 | 14.74 | 1686 | 16.95 | 1776 | 19.38
10894 | 2600 | 999 | 3.71 | 1058 | 4.57 | 1115 | 5.45 | 1169 | 6.33 | 1272 | 8.14 | 1369 | 10.02 | 1461 | 11.95 | 1549 | 13.97 | 1633 | 16.07 | 1714 | 18.25 | 1795 | 20.6
11732 | 2800 | 1066 | 4.47 | 1122 | 5.41 | 1176 | 6.35 | 1227 | 7.29 | 1325 | 9.22 | 1418 | 11.22 | 1506 | 13.26 | 1590 | 15.36 | 1671 | 17.53 | 1750 | 19.82 | 1825 | 22.13
12570 | 3000 | 1135 | 5.36 | 1187 | 6.36 | 1238 | 7.37 | 1287 | 8.38 | 1380 | 10.42 | 1469 | 12.53 | 1553 | 14.68 | 1634 | 16.88 | 1712 | 19.14 | 1788 | 21.49 | 1862 | 23.93
14246 | 3400 | 1272 | 7.47 | 1320 | 8.62 | 1365 | 9.75 | 1409 | 10.88 | 1495 | 13.19 | 1576 | 15.53 | 1654 | 17.9 | 1729 | 20.32 | 1802 | 22.81 | 1872 | 25.3 | 1941 | 27.89
15922 | 3800 | 1412 | 10.14 | 1454 | 11.39 | 1495 | 12.65 | 1536 | 13.94 | 1614 | 16.48 | 1689 | 19.05 | 1762 | 21.7 | 1832 | 24.35 | 1900 | 27.04 | 1966 | 29.78 | 2030 | 32.54
17598 | 4200 | 1551 | 13.36 | 1590 | 14.76 | 1628 | 16.16 | 1665 | 17.56 | 1737 | 20.37 | 1807 | 23.2 | 1875 | 26.08 | 1940 | 28.96 | 2004 | 31.89 | 2066 | 34.85 | 2127 | 37.86
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
10056 | 2400 | 1869 | 22.11
10894 | 2600 | 1876 | 23.09 | 1961 | 25.89 | 2048 | 28.95
11732 | 2800 | 1900 | 24.59 | 1975 | 27.19 | 2052 | 30.02 | 2131 | 33.09 | 2212 | 36.43
12570 | 3000 | 1933 | 26.41 | 2002 | 28.95 | 2072 | 31.67 | 2142 | 34.51 | 2215 | 37.64 | 2289 | 40.97 | 2365 | 44.56
13408 | 3200 | 1969 | 28.38 | 2036 | 31 | 2102 | 33.72 | 2167 | 36.51 | 2233 | 39.48 | 2299 | 42.56 | 2367 | 45.89 | 2437 | 49.48 | 2508 | 53.28
14246 | 3400 | 2008 | 30.53 | 2074 | 33.27 | 2138 | 36.06 | 2200 | 38.88 | 2261 | 41.76 | 2323 | 44.82 | 2385 | 48 | 2447 | 51.29 | 2511 | 54.82 | 2577 | 58.62 | 2644 | 62.64
15084 | 3600 | 2049 | 32.84 | 2113 | 35.64 | 2175 | 38.49 | 2236 | 41.42 | 2296 | 44.43 | 2354 | 47.44 | 2412 | 50.56 | 2470 | 53.79 | 2528 | 57.13 | 2588 | 60.71 | 2648 | 64.4
15922 | 3800 | 2093 | 35.36 | 2154 | 38.2 | 2215 | 41.16 | 2274 | 44.13 | 2333 | 47.25 | 2390 | 50.36 | 2445 | 53.47 | 2501 | 56.76 | 2556 | 60.08 | 2610 | 63.44 | 2666 | 67.04
16760 | 4000 | 2139 | 38.07 | 2198 | 40.98 | 2257 | 44.01 | 2314 | 47.04 | 2371 | 50.19 | 2427 | 53.4 | 2482 | 56.68 | 2536 | 60 | 2588 | 63.28 | 2641 | 66.75 | 2693 | 70.24
17598 | 4200 | 2186 | 40.89 | 2244 | 43.96 | 2301 | 47.06 | 2357 | 50.21 | 2412 | 53.41 | 2466 | 56.65 | 2520 | 60.01 | 2573 | 63.42 | 2625 | 66.88 | 2675 | 70.29 | 2726 | 73.88
19274 | 4600 | 2285 | 47.08 | 2340 | 50.38 | 2394 | 53.71 | 2448 | 57.13 | 2500 | 60.5 | 2551 | 63.89 | 2602 | 67.38 | 2652 | 70.9 | 2702 | 74.52 | 2751 | 78.16 | 2799 | 81.84
20950 | 5000 | 2390 | 54.1 | 2442 | 57.59 | 2493 | 61.11 | 2544 | 64.73 | 2594 | 68.37 | 2643 | 72.02 | 2691 | 75.66 | 2739 | 79.38 | 2786 | 83.11 | 2833 | 86.92 | 2879 | 90.74
High-pressure range
3000CEB
Outlet Area 5.17 ft² ¦ Wheel Dia. 30.00 in ¦ Tip Speed 7.85 × RPM (ft/min) ¦ Max BHP = 6.86 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 1257 Class II — 1623 Class III — 2059 Class IV — 2290
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
4136 | 800 | 411 | 0.45 | 533 | 0.89
4653 | 900 | 431 | 0.53 | 543 | 0.98 | 652 | 1.57
5170 | 1000 | 453 | 0.62 | 558 | 1.09 | 653 | 1.64
6204 | 1200 | 501 | 0.84 | 595 | 1.38 | 680 | 1.96 | 758 | 2.61
7238 | 1400 | 552 | 1.12 | 638 | 1.73 | 715 | 2.36 | 787 | 3.05 | 923 | 4.63
8272 | 1600 | 606 | 1.47 | 684 | 2.15 | 756 | 2.86 | 823 | 3.6 | 946 | 5.2 | 1065 | 7.08
9306 | 1800 | 662 | 1.9 | 734 | 2.65 | 801 | 3.44 | 863 | 4.24 | 979 | 5.94 | 1085 | 7.79 | 1192 | 9.95 | 1304 | 12.53
10340 | 2000 | 720 | 2.42 | 786 | 3.24 | 848 | 4.09 | 906 | 4.96 | 1015 | 6.78 | 1117 | 8.75 | 1212 | 10.84 | 1307 | 13.18 | 1408 | 15.98
11374 | 2200 | 778 | 3.02 | 840 | 3.93 | 898 | 4.86 | 953 | 5.8 | 1056 | 7.76 | 1152 | 9.81 | 1242 | 11.98 | 1329 | 14.31 | 1415 | 16.84 | 1505 | 19.75
12408 | 2400 | 838 | 3.74 | 895 | 4.72 | 950 | 5.73 | 1002 | 6.76 | 1099 | 8.84 | 1190 | 11 | 1277 | 13.29 | 1359 | 15.67 | 1438 | 18.18 | 1517 | 20.9 | 1598 | 23.91
13442 | 2600 | 898 | 4.56 | 952 | 5.64 | 1003 | 6.71 | 1052 | 7.81 | 1145 | 10.05 | 1232 | 12.36 | 1314 | 14.73 | 1394 | 17.24 | 1470 | 19.85 | 1543 | 22.55 | 1615 | 25.4
14476 | 2800 | 959 | 5.51 | 1010 | 6.68 | 1058 | 7.84 | 1104 | 8.99 | 1192 | 11.37 | 1276 | 13.84 | 1355 | 16.36 | 1430 | 18.92 | 1504 | 21.64 | 1575 | 24.46 | 1643 | 27.34
15510 | 3000 | 1021 | 6.61 | 1068 | 7.84 | 1114 | 9.09 | 1158 | 10.33 | 1242 | 12.87 | 1321 | 15.43 | 1397 | 18.09 | 1470 | 20.82 | 1540 | 23.59 | 1609 | 26.51 | 1675 | 29.5
17578 | 3400 | 1145 | 9.23 | 1187 | 10.62 | 1228 | 12.02 | 1268 | 13.43 | 1345 | 16.27 | 1418 | 19.15 | 1488 | 22.08 | 1556 | 25.08 | 1621 | 28.12 | 1685 | 31.25 | 1746 | 34.37
19646 | 3800 | 1270 | 12.5 | 1308 | 14.05 | 1345 | 15.6 | 1382 | 17.2 | 1452 | 20.32 | 1520 | 23.52 | 1585 | 26.75 | 1648 | 30.02 | 1709 | 33.33 | 1769 | 36.74 | 1827 | 40.17
21714 | 4200 | 1396 | 16.5 | 1430 | 18.19 | 1465 | 19.95 | 1498 | 21.66 | 1563 | 25.13 | 1626 | 28.63 | 1687 | 32.17 | 1746 | 35.75 | 1803 | 39.34 | 1859 | 42.99 | 1913 | 46.65
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
12408 | 2400 | 1682 | 27.28
13442 | 2600 | 1688 | 28.47 | 1765 | 31.96 | 1843 | 35.72
14476 | 2800 | 1710 | 30.36 | 1777 | 33.54 | 1847 | 37.06 | 1918 | 40.85 | 1991 | 44.97
15510 | 3000 | 1739 | 32.56 | 1802 | 35.75 | 1865 | 39.1 | 1928 | 42.61 | 1993 | 46.42 | 2060 | 50.56 | 2129 | 55.04
16544 | 3200 | 1772 | 35.02 | 1833 | 38.31 | 1892 | 41.63 | 1950 | 45.05 | 2009 | 48.68 | 2069 | 52.53 | 2131 | 56.7 | 2194 | 61.13 | 2257 | 65.74
17578 | 3400 | 1807 | 37.67 | 1866 | 41.03 | 1923 | 44.43 | 1980 | 47.99 | 2035 | 51.56 | 2090 | 55.27 | 2146 | 59.21 | 2202 | 63.28 | 2260 | 67.68 | 2319 | 72.33 | 2379 | 77.26
18612 | 3600 | 1844 | 40.53 | 1901 | 43.95 | 1958 | 47.55 | 2012 | 51.1 | 2066 | 54.81 | 2118 | 58.51 | 2171 | 62.43 | 2223 | 66.4 | 2275 | 70.5 | 2329 | 74.92 | 2383 | 79.48
19646 | 3800 | 1883 | 43.61 | 1939 | 47.18 | 1993 | 50.77 | 2047 | 54.51 | 2099 | 58.26 | 2150 | 62.08 | 2201 | 66.05 | 2250 | 69.97 | 2300 | 74.12 | 2349 | 78.3 | 2399 | 82.71
20680 | 4000 | 1924 | 46.91 | 1978 | 50.58 | 2031 | 54.31 | 2083 | 58.1 | 2134 | 61.96 | 2184 | 65.89 | 2233 | 69.88 | 2282 | 74.02 | 2329 | 78.1 | 2376 | 82.3 | 2423 | 86.63
21714 | 4200 | 1967 | 50.45 | 2019 | 54.22 | 2070 | 58.02 | 2121 | 61.96 | 2170 | 65.85 | 2219 | 69.89 | 2268 | 74.08 | 2315 | 78.22 | 2362 | 82.5 | 2407 | 86.71 | 2453 | 91.15
23782 | 4600 | 2056 | 58.08 | 2106 | 62.19 | 2154 | 66.25 | 2202 | 70.41 | 2249 | 74.59 | 2296 | 78.88 | 2341 | 83.09 | 2386 | 87.43 | 2431 | 91.89 | 2475 | 96.38 | 2519 | 101.01
25850 | 5000 | 2150 | 66.69 | 2197 | 71.02 | 2243 | 75.38 | 2289 | 79.85 | 2334 | 84.34 | 2378 | 88.83 | 2422 | 93.41 | 2465 | 97.98 | 2507 | 102.54 | 2549 | 107.21 | 2590 | 111.87
High-pressure range
3300CEB
Outlet Area 6.26 ft² ¦ Wheel Dia. 33.00 in ¦ Tip Speed 8.64 × RPM (ft/min) ¦ Max BHP = 11.05 × (RPM/1000)³ ¦ FEG80
MAXIMUM RPM: Class I — 1143 Class II — 1475 Class III — 1871 Class IV — 2081
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
5008 | 800 | 374 | 0.54 | 484 | 1.07
5634 | 900 | 392 | 0.64 | 493 | 1.18 | 593 | 1.9
6260 | 1000 | 412 | 0.75 | 508 | 1.33 | 594 | 1.99
7512 | 1200 | 455 | 1.02 | 541 | 1.67 | 618 | 2.37 | 690 | 3.17
8764 | 1400 | 502 | 1.36 | 580 | 2.09 | 650 | 2.86 | 716 | 3.7 | 839 | 5.6
10016 | 1600 | 551 | 1.78 | 622 | 2.6 | 688 | 3.47 | 748 | 4.35 | 860 | 6.3 | 968 | 8.56
11268 | 1800 | 602 | 2.3 | 668 | 3.22 | 728 | 4.16 | 785 | 5.14 | 890 | 7.19 | 987 | 9.45 | 1083 | 12.02 | 1186 | 15.19
12520 | 2000 | 655 | 2.93 | 715 | 3.93 | 771 | 4.96 | 824 | 6.01 | 923 | 8.21 | 1015 | 10.57 | 1102 | 13.13 | 1188 | 15.95 | 1280 | 19.34
13772 | 2200 | 708 | 3.66 | 764 | 4.77 | 817 | 5.89 | 867 | 7.04 | 960 | 9.39 | 1047 | 11.86 | 1130 | 14.53 | 1208 | 17.31 | 1286 | 20.37 | 1368 | 23.89
15024 | 2400 | 762 | 4.52 | 814 | 5.72 | 864 | 6.95 | 911 | 8.18 | 1000 | 10.72 | 1082 | 13.32 | 1161 | 16.09 | 1236 | 18.99 | 1308 | 22.04 | 1379 | 25.29 | 1453 | 28.95
16276 | 2600 | 817 | 5.53 | 866 | 6.84 | 912 | 8.13 | 957 | 9.47 | 1041 | 12.17 | 1120 | 14.96 | 1195 | 17.84 | 1267 | 20.85 | 1336 | 24 | 1403 | 27.31 | 1468 | 30.73
17528 | 2800 | 873 | 6.7 | 918 | 8.08 | 962 | 9.49 | 1004 | 10.89 | 1084 | 13.77 | 1160 | 16.75 | 1232 | 19.81 | 1301 | 22.95 | 1367 | 26.17 | 1432 | 29.61 | 1494 | 33.11
18780 | 3000 | 929 | 8.02 | 972 | 9.52 | 1013 | 11.01 | 1053 | 12.51 | 1129 | 15.56 | 1202 | 18.73 | 1271 | 21.95 | 1337 | 25.23 | 1401 | 28.61 | 1463 | 32.1 | 1523 | 35.72
21284 | 3400 | 1041 | 11.17 | 1080 | 12.88 | 1117 | 14.57 | 1153 | 16.26 | 1223 | 19.7 | 1290 | 23.22 | 1353 | 26.73 | 1415 | 30.38 | 1474 | 34.05 | 1532 | 37.83 | 1588 | 41.65
23788 | 3800 | 1155 | 15.14 | 1190 | 17.04 | 1224 | 18.94 | 1257 | 20.84 | 1321 | 24.65 | 1382 | 28.47 | 1441 | 32.37 | 1499 | 36.38 | 1554 | 40.36 | 1608 | 44.45 | 1661 | 48.62
26292 | 4200 | 1270 | 20.01 | 1301 | 22.05 | 1332 | 24.14 | 1363 | 26.28 | 1422 | 30.48 | 1479 | 34.7 | 1534 | 38.95 | 1587 | 43.24 | 1640 | 47.68 | 1690 | 52.02 | 1740 | 56.54
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
15024 | 2400 | 1529 | 33.02
16276 | 2600 | 1535 | 34.49 | 1605 | 38.71 | 1676 | 43.27
17528 | 2800 | 1555 | 36.77 | 1616 | 40.63 | 1679 | 44.85 | 1744 | 49.47 | 1810 | 54.43
18780 | 3000 | 1581 | 39.42 | 1638 | 43.25 | 1695 | 47.29 | 1753 | 51.6 | 1812 | 56.2 | 1873 | 61.22 | 1935 | 66.58
20032 | 3200 | 1611 | 42.39 | 1666 | 46.33 | 1720 | 50.39 | 1773 | 54.54 | 1827 | 58.98 | 1881 | 63.59 | 1937 | 68.59 | 1994 | 73.93 | 2052 | 79.59
21284 | 3400 | 1643 | 45.61 | 1697 | 49.71 | 1749 | 53.84 | 1800 | 58.08 | 1850 | 62.4 | 1900 | 66.9 | 1951 | 71.67 | 2002 | 76.61 | 2055 | 81.96 | 2108 | 87.52 | 2163 | 93.54
22536 | 3600 | 1677 | 49.1 | 1729 | 53.27 | 1780 | 57.55 | 1830 | 61.94 | 1878 | 66.31 | 1926 | 70.87 | 1974 | 75.59 | 2021 | 80.37 | 2069 | 85.42 | 2117 | 90.64 | 2167 | 96.28
23788 | 3800 | 1712 | 52.79 | 1763 | 57.12 | 1812 | 61.45 | 1861 | 65.98 | 1909 | 70.6 | 1955 | 75.19 | 2001 | 79.95 | 2046 | 84.75 | 2091 | 89.72 | 2136 | 94.84 | 2181 | 100.11
25040 | 4000 | 1750 | 56.85 | 1799 | 61.29 | 1847 | 65.79 | 1894 | 70.35 | 1940 | 74.99 | 1986 | 79.81 | 2031 | 84.7 | 2075 | 89.64 | 2118 | 94.61 | 2161 | 99.74 | 2203 | 104.88
26292 | 4200 | 1789 | 61.13 | 1836 | 65.67 | 1883 | 70.35 | 1929 | 75.07 | 1974 | 79.85 | 2018 | 84.67 | 2062 | 89.67 | 2105 | 94.72 | 2148 | 99.95 | 2189 | 105.05 | 2230 | 110.31
28796 | 4600 | 1870 | 70.39 | 1915 | 75.31 | 1959 | 80.27 | 2003 | 85.36 | 2045 | 90.32 | 2087 | 95.42 | 2129 | 100.67 | 2170 | 105.93 | 2211 | 111.36 | 2251 | 116.79 | 2290 | 122.24
31300 | 5000 | 1955 | 80.75 | 1998 | 86.04 | 2040 | 91.33 | 2082 | 96.78 | 2122 | 102.09 | 2163 | 107.67 | 2202 | 113.06 | 2241 | 118.59 | 2280 | 124.24 | 2318 | 129.87 | 2355 | 135.47
High-pressure range
3650CEB
Outlet Area 7.66 ft² ¦ Wheel Dia. 36.50 in ¦ Tip Speed 9.56 × RPM (ft/min) ¦ Max BHP = 19.42 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 995 Class II — 1283 Class III — 1727 Class IV — 1883
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
6128 | 800 | 326 | 0.65 | 430 | 1.27
6894 | 900 | 342 | 0.76 | 435 | 1.41
7660 | 1000 | 359 | 0.89 | 445 | 1.58 | 527 | 2.37
9192 | 1200 | 397 | 1.2 | 472 | 1.99 | 543 | 2.86 | 610 | 3.77
10724 | 1400 | 439 | 1.6 | 505 | 2.48 | 567 | 3.41 | 628 | 4.44 | 744 | 6.63
12256 | 1600 | 483 | 2.09 | 542 | 3.07 | 598 | 4.09 | 653 | 5.2 | 758 | 7.57 | 859 | 10.14
13788 | 1800 | 529 | 2.7 | 582 | 3.77 | 633 | 4.89 | 683 | 6.08 | 779 | 8.62 | 871 | 11.33 | 961 | 14.26
15320 | 2000 | 577 | 3.46 | 625 | 4.61 | 671 | 5.82 | 717 | 7.09 | 805 | 9.79 | 890 | 12.68 | 972 | 15.7 | 1053 | 18.93
16852 | 2200 | 625 | 4.34 | 669 | 5.58 | 712 | 6.9 | 754 | 8.26 | 836 | 11.14 | 915 | 14.2 | 992 | 17.44 | 1066 | 20.75 | 1139 | 24.23 | 1215 | 28.13
18384 | 2400 | 674 | 5.38 | 715 | 6.73 | 754 | 8.11 | 793 | 9.58 | 869 | 12.62 | 943 | 15.85 | 1015 | 19.26 | 1085 | 22.79 | 1153 | 26.39 | 1221 | 30.22 | 1289 | 34.27
19916 | 2600 | 724 | 6.62 | 761 | 8.02 | 798 | 9.52 | 835 | 11.1 | 906 | 14.34 | 975 | 17.72 | 1042 | 21.26 | 1108 | 24.97 | 1173 | 28.83 | 1236 | 32.73 | 1298 | 36.75
21448 | 2800 | 774 | 8.03 | 809 | 9.54 | 843 | 11.1 | 877 | 12.75 | 944 | 16.2 | 1009 | 19.76 | 1073 | 23.51 | 1135 | 27.37 | 1196 | 31.37 | 1256 | 35.49 | 1315 | 39.71
22980 | 3000 | 824 | 9.62 | 857 | 11.24 | 889 | 12.89 | 921 | 14.63 | 984 | 18.27 | 1045 | 22 | 1106 | 25.94 | 1165 | 29.99 | 1222 | 34.09 | 1279 | 38.39 | 1336 | 42.89
26044 | 3400 | 926 | 13.52 | 955 | 15.32 | 984 | 17.18 | 1012 | 19.07 | 1068 | 23.06 | 1123 | 27.2 | 1177 | 31.44 | 1231 | 35.86 | 1283 | 40.32 | 1335 | 44.99 | 1386 | 49.74
29108 | 3800 | 1028 | 18.37 | 1054 | 20.35 | 1080 | 22.39 | 1106 | 24.51 | 1157 | 28.87 | 1206 | 33.33 | 1255 | 37.97 | 1304 | 42.75 | 1352 | 47.6 | 1399 | 52.51 | 1446 | 57.62
32172 | 4200 | 1131 | 24.32 | 1155 | 26.52 | 1179 | 28.79 | 1202 | 31.04 | 1248 | 35.72 | 1293 | 40.54 | 1338 | 45.58 | 1383 | 50.78 | 1427 | 56 | 1470 | 61.24 | 1514 | 66.76
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
18384 | 2400 | 1359 | 38.63
19916 | 2600 | 1361 | 41.06 | 1424 | 45.55
21448 | 2800 | 1373 | 44.01 | 1430 | 48.4 | 1489 | 53.19 | 1549 | 58.22
22980 | 3000 | 1391 | 47.35 | 1445 | 51.88 | 1499 | 56.57 | 1553 | 61.45 | 1607 | 66.5 | 1664 | 72.04
24512 | 3200 | 1412 | 50.85 | 1464 | 55.62 | 1515 | 60.42 | 1566 | 65.38 | 1616 | 70.37 | 1667 | 75.67 | 1718 | 81.13 | 1771 | 86.98
26044 | 3400 | 1436 | 54.56 | 1486 | 59.55 | 1535 | 64.57 | 1584 | 69.73 | 1631 | 74.77 | 1679 | 80.1 | 1727 | 85.59 | 1774 | 91.09 | 1823 | 97.05 | 1872 | 103.1 | 1922 | 109.44
27576 | 3600 | 1463 | 58.56 | 1511 | 63.73 | 1558 | 68.95 | 1605 | 74.31 | 1651 | 79.67 | 1696 | 85.02 | 1741 | 90.5 | 1786 | 96.12 | 1831 | 101.9 | 1876 | 107.83 | 1922 | 114.08
29108 | 3800 | 1492 | 62.79 | 1538 | 68.13 | 1583 | 73.5 | 1628 | 79.02 | 1672 | 84.54 | 1716 | 90.2 | 1760 | 95.98 | 1803 | 101.73 | 1845 | 107.43 | 1888 | 113.45 | 1930 | 119.43
30640 | 4000 | 1523 | 67.32 | 1567 | 72.79 | 1611 | 78.43 | 1654 | 84.09 | 1697 | 89.89 | 1739 | 95.68 | 1781 | 101.6 | 1822 | 107.46 | 1863 | 113.44 | 1904 | 119.54 | 1945 | 125.78
32172 | 4200 | 1556 | 72.18 | 1599 | 77.92 | 1640 | 83.52 | 1682 | 89.43 | 1723 | 95.34 | 1764 | 101.38 | 1804 | 107.39 | 1844 | 113.53 | 1884 | 119.79 | 1924 | 126.17 | 1963 | 132.47
35236 | 4600 | 1626 | 82.84 | 1666 | 88.9 | 1705 | 94.96 | 1743 | 101.01 | 1782 | 107.39 | 1820 | 113.74 | 1857 | 120.02 | 1895 | 126.64 | 1932 | 133.19 | 1969 | 139.86 | 2006 | 146.66
38300 | 5000 | 1701 | 94.86 | 1738 | 101.23 | 1774 | 107.55 | 1811 | 114.19 | 1847 | 120.79 | 1882 | 127.34 | 1918 | 134.23 | 1953 | 141.06 | 1988 | 148.01 | 2022 | 154.86 | 2057 | 162.06
High-pressure range
4025CEB
Outlet Area 9.31 ft² ¦ Wheel Dia. 40.25 in ¦ Tip Speed 10.54 × RPM (ft/min) ¦ Max BHP = 31.67 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 903 Class II — 1163 Class III — 1566 Class IV — 1706
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
9112 | 800 | 268 | 0.97 | 352 | 1.88
10251 | 900 | 280 | 1.13 | 357 | 2.1
11390 | 1000 | 294 | 1.32 | 365 | 2.36 | 432 | 3.52
13668 | 1200 | 325 | 1.78 | 387 | 2.95 | 445 | 4.24 | 501 | 5.62
15946 | 1400 | 360 | 2.38 | 414 | 3.68 | 466 | 5.1 | 515 | 6.59 | 611 | 9.9
18224 | 1600 | 396 | 3.1 | 444 | 4.54 | 491 | 6.1 | 536 | 7.75 | 621 | 11.21 | 705 | 15.11
20502 | 1800 | 434 | 4.02 | 478 | 5.62 | 520 | 7.3 | 560 | 9.02 | 639 | 12.81 | 714 | 16.82 | 788 | 21.18
22780 | 2000 | 473 | 5.13 | 513 | 6.87 | 551 | 8.67 | 588 | 10.54 | 661 | 14.59 | 730 | 18.85 | 798 | 23.4 | 864 | 28.18
25058 | 2200 | 513 | 6.46 | 549 | 8.3 | 584 | 10.26 | 619 | 12.32 | 686 | 16.58 | 750 | 21.07 | 813 | 25.87 | 874 | 30.81 | 935 | 36.12 | 996 | 41.75
27336 | 2400 | 553 | 8.01 | 586 | 9.97 | 619 | 12.09 | 651 | 14.28 | 713 | 18.77 | 774 | 23.61 | 833 | 28.67 | 890 | 33.88 | 946 | 39.27 | 1001 | 44.86 | 1057 | 50.91
29614 | 2600 | 594 | 9.84 | 625 | 11.96 | 655 | 14.17 | 685 | 16.51 | 743 | 21.3 | 800 | 26.37 | 855 | 31.63 | 909 | 37.14 | 962 | 42.84 | 1014 | 48.69 | 1065 | 54.68
31892 | 2800 | 635 | 11.94 | 664 | 14.2 | 692 | 16.54 | 720 | 19.01 | 774 | 24.06 | 828 | 29.41 | 880 | 34.93 | 931 | 40.69 | 981 | 46.64 | 1030 | 52.73 | 1079 | 59.1
34170 | 3000 | 676 | 14.31 | 703 | 16.71 | 730 | 19.23 | 756 | 21.8 | 807 | 27.15 | 858 | 32.8 | 907 | 38.54 | 955 | 44.5 | 1003 | 50.78 | 1050 | 57.22 | 1096 | 63.78
38726 | 3400 | 760 | 20.14 | 784 | 22.82 | 807 | 25.53 | 830 | 28.33 | 876 | 34.27 | 921 | 40.42 | 966 | 46.82 | 1010 | 53.36 | 1053 | 60.05 | 1095 | 66.87 | 1137 | 73.97
43282 | 3800 | 844 | 27.38 | 865 | 30.29 | 886 | 33.3 | 907 | 36.4 | 949 | 42.91 | 990 | 49.66 | 1030 | 56.54 | 1070 | 63.62 | 1109 | 70.76 | 1148 | 78.16 | 1186 | 85.65
47838 | 4200 | 928 | 36.19 | 948 | 39.5 | 967 | 42.79 | 986 | 46.15 | 1024 | 53.14 | 1061 | 60.34 | 1098 | 67.84 | 1134 | 75.4 | 1170 | 83.14 | 1206 | 91.09 | 1242 | 99.27
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
27336 | 2400 | 1115 | 57.49
29614 | 2600 | 1116 | 60.99 | 1168 | 67.72
31892 | 2800 | 1126 | 65.39 | 1173 | 71.97 | 1221 | 79.01 | 1270 | 86.46
34170 | 3000 | 1141 | 70.41 | 1185 | 77.08 | 1229 | 84 | 1274 | 91.4 | 1318 | 98.85 | 1364 | 106.91
36448 | 3200 | 1158 | 75.57 | 1201 | 82.72 | 1243 | 89.9 | 1284 | 97.09 | 1326 | 104.75 | 1367 | 112.43 | 1409 | 120.59 | 1453 | 129.42
38726 | 3400 | 1178 | 81.14 | 1219 | 88.55 | 1259 | 95.98 | 1299 | 103.61 | 1338 | 111.22 | 1377 | 119.04 | 1416 | 127.1 | 1455 | 135.41 | 1495 | 144.22 | 1535 | 153.16 | 1576 | 162.57
41004 | 3600 | 1200 | 87.05 | 1239 | 94.66 | 1278 | 102.52 | 1316 | 110.36 | 1354 | 118.39 | 1391 | 126.36 | 1428 | 134.54 | 1465 | 142.93 | 1502 | 151.54 | 1539 | 160.39 | 1576 | 169.46
43282 | 3800 | 1224 | 93.39 | 1262 | 101.4 | 1299 | 109.41 | 1335 | 117.38 | 1372 | 125.84 | 1408 | 134.23 | 1443 | 142.51 | 1479 | 151.27 | 1514 | 159.94 | 1548 | 168.48 | 1583 | 177.55
45560 | 4000 | 1250 | 100.25 | 1286 | 108.39 | 1321 | 116.49 | 1357 | 125.09 | 1392 | 133.65 | 1426 | 142.12 | 1461 | 151.09 | 1495 | 159.93 | 1528 | 168.62 | 1562 | 177.82 | 1595 | 186.87
47838 | 4200 | 1277 | 107.47 | 1311 | 115.68 | 1346 | 124.39 | 1380 | 133.05 | 1413 | 141.64 | 1447 | 150.75 | 1480 | 159.75 | 1513 | 168.94 | 1546 | 178.33 | 1578 | 187.53 | 1610 | 196.89
52394 | 4600 | 1334 | 123.22 | 1366 | 132 | 1398 | 141.01 | 1430 | 150.26 | 1462 | 159.75 | 1493 | 169.13 | 1524 | 178.72 | 1554 | 188.14 | 1585 | 198.11 | 1615 | 207.9 | 1645 | 217.87
56950 | 5000 | 1396 | 141.24 | 1426 | 150.61 | 1456 | 160.17 | 1485 | 169.59 | 1515 | 179.56 | 1544 | 189.41 | 1573 | 199.46 | 1602 | 209.72 | 1630 | 219.77 | 1659 | 230.41 | 1687 | 240.82
High-pressure range
4450CEB
Outlet Area 11.39 ft² ¦ Wheel Dia. 44.50 in ¦ Tip Speed 11.65 × RPM (ft/min) ¦ Max BHP = 52.32 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 817 Class II — 1052 Class III — 1416 Class IV — 1545
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
7448 | 800 | 296 | 0.79 | 390 | 1.55
8379 | 900 | 310 | 0.93 | 395 | 1.72
9310 | 1000 | 325 | 1.08 | 404 | 1.93 | 478 | 2.89
11172 | 1200 | 360 | 1.46 | 428 | 2.42 | 492 | 3.46 | 553 | 4.58
13034 | 1400 | 398 | 1.94 | 457 | 2.99 | 515 | 4.17 | 569 | 5.38 | 675 | 8.08
14896 | 1600 | 438 | 2.54 | 491 | 3.72 | 542 | 4.97 | 592 | 6.32 | 687 | 9.18 | 779 | 12.33
16758 | 1800 | 480 | 3.29 | 528 | 4.59 | 574 | 5.94 | 619 | 7.38 | 706 | 10.46 | 789 | 13.73 | 871 | 17.31
18620 | 2000 | 523 | 4.2 | 566 | 5.58 | 609 | 7.09 | 650 | 8.62 | 730 | 11.9 | 807 | 15.41 | 882 | 19.12 | 955 | 23.02
20482 | 2200 | 567 | 5.28 | 607 | 6.8 | 645 | 8.37 | 684 | 10.06 | 758 | 13.54 | 829 | 17.22 | 899 | 21.17 | 966 | 25.17 | 1033 | 29.47 | 1102 | 34.21
22344 | 2400 | 611 | 6.54 | 648 | 8.17 | 684 | 9.88 | 719 | 11.64 | 788 | 15.34 | 855 | 19.26 | 920 | 23.38 | 984 | 27.71 | 1046 | 32.13 | 1107 | 36.71 | 1169 | 41.67
24206 | 2600 | 656 | 8.03 | 690 | 9.75 | 724 | 11.59 | 757 | 13.49 | 821 | 17.4 | 884 | 21.53 | 945 | 25.85 | 1005 | 30.38 | 1064 | 35.08 | 1121 | 39.81 | 1177 | 44.66
26068 | 2800 | 702 | 9.76 | 733 | 11.57 | 765 | 13.53 | 795 | 15.49 | 856 | 19.7 | 915 | 24.03 | 973 | 28.58 | 1029 | 33.25 | 1084 | 38.08 | 1139 | 43.16 | 1192 | 48.21
27930 | 3000 | 747 | 11.69 | 777 | 13.66 | 806 | 15.67 | 835 | 17.78 | 892 | 22.2 | 948 | 26.79 | 1002 | 31.46 | 1056 | 36.42 | 1108 | 41.44 | 1160 | 46.7 | 1211 | 52.07
31654 | 3400 | 839 | 16.4 | 866 | 18.62 | 892 | 20.87 | 918 | 23.21 | 968 | 27.99 | 1018 | 33.04 | 1067 | 38.2 | 1116 | 43.57 | 1163 | 48.97 | 1210 | 54.62 | 1257 | 60.49
35378 | 3800 | 932 | 22.32 | 956 | 24.76 | 979 | 27.2 | 1003 | 29.81 | 1048 | 34.99 | 1093 | 40.46 | 1138 | 46.16 | 1182 | 51.92 | 1226 | 57.87 | 1269 | 63.91 | 1311 | 70.02
39102 | 4200 | 1025 | 29.52 | 1047 | 32.22 | 1068 | 34.9 | 1089 | 37.65 | 1131 | 43.35 | 1173 | 49.37 | 1213 | 55.38 | 1253 | 61.58 | 1293 | 67.93 | 1333 | 74.46 | 1372 | 81.01
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
22344 | 2400 | 1233 | 47.03
24206 | 2600 | 1234 | 49.89 | 1292 | 55.45
26068 | 2800 | 1245 | 53.49 | 1297 | 58.86 | 1350 | 64.62 | 1404 | 70.67
27930 | 3000 | 1261 | 57.51 | 1310 | 63.01 | 1359 | 68.72 | 1408 | 74.65 | 1458 | 80.96 | 1509 | 87.57
29792 | 3200 | 1280 | 61.76 | 1327 | 67.53 | 1374 | 73.48 | 1420 | 79.46 | 1466 | 85.65 | 1512 | 92.05 | 1558 | 98.64 | 1606 | 105.73
31654 | 3400 | 1302 | 66.3 | 1347 | 72.31 | 1392 | 78.5 | 1436 | 84.7 | 1479 | 90.9 | 1522 | 97.27 | 1566 | 104.03 | 1609 | 110.79 | 1653 | 117.94 | 1698 | 125.42 | 1743 | 133.04
33516 | 3600 | 1327 | 71.25 | 1370 | 77.45 | 1413 | 83.85 | 1455 | 90.26 | 1497 | 96.83 | 1538 | 103.36 | 1579 | 110.06 | 1619 | 116.73 | 1660 | 123.78 | 1701 | 131.03 | 1743 | 138.69
35378 | 3800 | 1353 | 76.35 | 1394 | 82.71 | 1435 | 89.27 | 1476 | 96.01 | 1516 | 102.74 | 1556 | 109.63 | 1596 | 116.68 | 1634 | 123.44 | 1673 | 130.58 | 1712 | 137.9 | 1750 | 145.14
37240 | 4000 | 1381 | 81.83 | 1421 | 88.51 | 1460 | 95.19 | 1499 | 102.06 | 1538 | 109.1 | 1577 | 116.33 | 1615 | 123.5 | 1652 | 130.59 | 1690 | 138.05 | 1726 | 145.18 | 1763 | 152.7
39102 | 4200 | 1411 | 87.76 | 1449 | 94.54 | 1487 | 101.52 | 1525 | 108.68 | 1562 | 115.81 | 1599 | 123.11 | 1636 | 130.59 | 1672 | 137.98 | 1708 | 145.52 | 1744 | 153.19 | 1779 | 160.74
42826 | 4600 | 1474 | 100.63 | 1510 | 107.93 | 1545 | 115.21 | 1581 | 122.92 | 1615 | 130.35 | 1650 | 138.18 | 1684 | 145.94 | 1718 | 153.86 | 1752 | 161.94 | 1785 | 169.89 | 1819 | 178.28
46550 | 5000 | 1542 | 115.24 | 1576 | 123.08 | 1609 | 130.85 | 1642 | 138.78 | 1674 | 146.63 | 1706 | 154.66 | 1739 | 163.14 | 1770 | 171.21 | 1802 | 179.73 | 1833 | 188.1 | 1865 | 196.93
High-pressure range
4900CEB
Outlet Area 13.80 ft² ¦ Wheel Dia. 49.00 in ¦ Tip Speed 12.83 × RPM (ft/min) ¦ Max BHP = 84.69 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 742 Class II — 956 Class III — 1286 Class IV — 1401
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
11040 | 800 | 243 | 1.17 | 320 | 2.29
12420 | 900 | 254 | 1.36 | 324 | 2.54
13800 | 1000 | 267 | 1.6 | 332 | 2.87 | 392 | 4.26
16560 | 1200 | 295 | 2.15 | 351 | 3.56 | 404 | 5.13 | 455 | 6.82
19320 | 1400 | 327 | 2.88 | 376 | 4.46 | 423 | 6.18 | 468 | 8.01 | 554 | 11.94
22080 | 1600 | 360 | 3.78 | 403 | 5.5 | 446 | 7.4 | 486 | 9.35 | 564 | 13.59 | 640 | 18.28
24840 | 1800 | 394 | 4.87 | 433 | 6.77 | 472 | 8.84 | 509 | 10.97 | 580 | 15.51 | 648 | 20.34 | 716 | 25.71
27600 | 2000 | 430 | 6.24 | 465 | 8.28 | 500 | 10.49 | 534 | 12.78 | 600 | 17.67 | 663 | 22.85 | 724 | 28.28 | 785 | 34.19
30360 | 2200 | 466 | 7.84 | 498 | 10.03 | 530 | 12.41 | 562 | 14.92 | 623 | 20.1 | 681 | 25.53 | 739 | 31.44 | 794 | 37.38 | 849 | 43.75 | 905 | 50.68
33120 | 2400 | 502 | 9.7 | 532 | 12.08 | 562 | 14.65 | 591 | 17.29 | 648 | 22.81 | 703 | 28.63 | 756 | 34.69 | 808 | 41.03 | 859 | 47.58 | 909 | 54.35 | 960 | 61.71
35880 | 2600 | 539 | 11.9 | 567 | 14.46 | 595 | 17.2 | 621 | 19.92 | 674 | 25.74 | 726 | 31.9 | 776 | 38.28 | 825 | 44.93 | 874 | 51.99 | 921 | 59.03 | 967 | 66.24
38640 | 2800 | 576 | 14.42 | 602 | 17.14 | 628 | 20.01 | 653 | 22.95 | 703 | 29.18 | 751 | 35.53 | 799 | 42.32 | 845 | 49.24 | 891 | 56.55 | 936 | 64.04 | 979 | 71.43
41400 | 3000 | 614 | 17.36 | 638 | 20.21 | 662 | 23.21 | 686 | 26.37 | 733 | 32.94 | 778 | 39.59 | 823 | 46.61 | 867 | 53.89 | 911 | 61.59 | 953 | 69.24 | 995 | 77.23
46920 | 3400 | 690 | 24.39 | 711 | 27.56 | 733 | 30.97 | 754 | 34.39 | 795 | 41.47 | 836 | 48.93 | 877 | 56.71 | 917 | 64.64 | 956 | 72.73 | 994 | 80.96 | 1032 | 89.52
52440 | 3800 | 766 | 33.13 | 785 | 36.65 | 805 | 40.44 | 824 | 44.19 | 861 | 51.88 | 898 | 60 | 935 | 68.46 | 971 | 76.97 | 1007 | 85.76 | 1042 | 94.61 | 1077 | 103.81
57960 | 4200 | 842 | 43.76 | 860 | 47.74 | 878 | 51.85 | 895 | 55.88 | 929 | 64.24 | 963 | 73.04 | 997 | 82.22 | 1030 | 91.46 | 1063 | 100.93 | 1095 | 110.36 | 1127 | 120.06
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
33120 | 2400 | 1012 | 69.54
35880 | 2600 | 1013 | 73.8 | 1061 | 82.13
38640 | 2800 | 1022 | 79.12 | 1066 | 87.4 | 1109 | 95.79 | 1154 | 104.95
41400 | 3000 | 1036 | 85.29 | 1076 | 93.38 | 1116 | 101.77 | 1157 | 110.77 | 1197 | 119.81 | 1239 | 129.64
44160 | 3200 | 1052 | 91.69 | 1090 | 100.07 | 1129 | 109.01 | 1166 | 117.65 | 1204 | 126.88 | 1242 | 136.43 | 1280 | 146.28 | 1319 | 156.63
46920 | 3400 | 1070 | 98.41 | 1107 | 107.33 | 1144 | 116.53 | 1180 | 125.68 | 1215 | 134.76 | 1251 | 144.44 | 1286 | 154.06 | 1322 | 164.33 | 1358 | 174.89 | 1394 | 185.59 | 1432 | 197.3
49680 | 3600 | 1090 | 105.59 | 1125 | 114.68 | 1160 | 124.06 | 1195 | 133.72 | 1229 | 143.27 | 1263 | 153.07 | 1297 | 163.12 | 1330 | 173.05 | 1364 | 183.64 | 1397 | 194.1 | 1431 | 205.25
52440 | 3800 | 1111 | 113.04 | 1146 | 122.89 | 1179 | 132.39 | 1213 | 142.5 | 1246 | 152.54 | 1278 | 162.43 | 1311 | 172.93 | 1343 | 183.28 | 1374 | 193.44 | 1406 | 204.27 | 1438 | 215.35
55200 | 4000 | 1135 | 121.48 | 1167 | 131.09 | 1200 | 141.33 | 1232 | 151.51 | 1264 | 161.95 | 1295 | 172.26 | 1326 | 182.8 | 1357 | 193.55 | 1388 | 204.52 | 1418 | 215.27 | 1448 | 226.25
57960 | 4200 | 1159 | 130.06 | 1191 | 140.38 | 1222 | 150.65 | 1253 | 161.2 | 1283 | 171.62 | 1314 | 182.69 | 1344 | 193.61 | 1374 | 204.77 | 1403 | 215.68 | 1433 | 227.26 | 1462 | 238.58
63480 | 4600 | 1211 | 149.21 | 1241 | 160.21 | 1270 | 171.11 | 1298 | 181.89 | 1327 | 193.36 | 1355 | 204.64 | 1383 | 216.16 | 1411 | 227.93 | 1439 | 239.94 | 1466 | 251.66 | 1494 | 264.13
69000 | 5000 | 1267 | 170.93 | 1294 | 182.17 | 1322 | 194.07 | 1348 | 205.33 | 1375 | 217.29 | 1402 | 229.53 | 1428 | 241.55 | 1454 | 253.79 | 1480 | 266.26 | 1506 | 278.96 | 1532 | 291.9
High-pressure range
5450CEB
Outlet Area 16.92 ft² ¦ Wheel Dia. 54.25 in ¦ Tip Speed 14.20 × RPM (ft/min) ¦ Max BHP = 140.88 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 670 Class II — 863 Class III — 1162 Class IV — 1260
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
13536 | 800 | 220 | 1.44 | 289 | 2.8
15228 | 900 | 230 | 1.68 | 293 | 3.13
16920 | 1000 | 241 | 1.95 | 300 | 3.52 | 354 | 5.22
20304 | 1200 | 267 | 2.65 | 317 | 4.37 | 365 | 6.29 | 411 | 8.36
23688 | 1400 | 295 | 3.52 | 339 | 5.44 | 382 | 7.57 | 423 | 9.83 | 501 | 14.69
27072 | 1600 | 325 | 4.62 | 364 | 6.74 | 403 | 9.08 | 439 | 11.46 | 510 | 16.72 | 578 | 22.41
30456 | 1800 | 356 | 5.97 | 392 | 8.35 | 426 | 10.81 | 460 | 13.46 | 524 | 19.02 | 586 | 25.03 | 646 | 31.42
33840 | 2000 | 388 | 7.62 | 420 | 10.15 | 452 | 12.9 | 482 | 15.63 | 542 | 21.66 | 599 | 28.03 | 654 | 34.68 | 709 | 41.92
37224 | 2200 | 421 | 9.62 | 450 | 12.32 | 479 | 15.24 | 507 | 18.22 | 562 | 24.55 | 616 | 31.44 | 667 | 38.46 | 717 | 45.8 | 767 | 53.67 | 817 | 62.03
40608 | 2400 | 454 | 11.94 | 481 | 14.85 | 508 | 18 | 534 | 21.22 | 585 | 27.92 | 635 | 35.1 | 683 | 42.56 | 730 | 50.34 | 776 | 58.36 | 821 | 66.62 | 867 | 75.63
43992 | 2600 | 487 | 14.61 | 512 | 17.71 | 537 | 21.03 | 561 | 24.43 | 609 | 31.59 | 656 | 39.14 | 701 | 46.94 | 746 | 55.27 | 789 | 63.63 | 832 | 72.41 | 873 | 81.08
47376 | 2800 | 521 | 17.75 | 544 | 21.03 | 567 | 24.5 | 590 | 28.16 | 635 | 35.77 | 679 | 43.68 | 722 | 51.95 | 764 | 60.54 | 805 | 69.38 | 845 | 78.39 | 885 | 87.79
50760 | 3000 | 555 | 21.33 | 577 | 24.87 | 598 | 28.46 | 620 | 32.38 | 662 | 40.36 | 703 | 48.59 | 744 | 57.28 | 784 | 66.29 | 822 | 75.26 | 861 | 84.95 | 899 | 94.77
57528 | 3400 | 623 | 29.87 | 643 | 33.91 | 662 | 37.95 | 681 | 42.14 | 719 | 51.02 | 756 | 60.2 | 792 | 69.48 | 828 | 79.16 | 863 | 89.01 | 898 | 99.31 | 932 | 109.69
64296 | 3800 | 692 | 40.63 | 709 | 44.92 | 727 | 49.54 | 744 | 54.11 | 778 | 63.67 | 812 | 73.79 | 845 | 84.06 | 877 | 94.33 | 910 | 105.27 | 941 | 115.91 | 973 | 127.34
71064 | 4200 | 761 | 53.74 | 777 | 58.57 | 793 | 63.54 | 809 | 68.65 | 840 | 78.99 | 870 | 89.58 | 900 | 100.61 | 930 | 111.99 | 960 | 123.67 | 989 | 135.27 | 1018 | 147.2
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
40608 | 2400 | 914 | 85.24
43992 | 2600 | 915 | 90.49 | 958 | 100.59
47376 | 2800 | 924 | 97.28 | 962 | 106.86 | 1002 | 117.55 | 1042 | 128.54
50760 | 3000 | 936 | 104.64 | 972 | 114.52 | 1008 | 124.77 | 1045 | 135.79 | 1082 | 147.22 | 1119 | 158.89
54144 | 3200 | 950 | 112.33 | 985 | 122.86 | 1019 | 133.34 | 1053 | 144.16 | 1087 | 155.34 | 1122 | 167.35 | 1156 | 179.27 | 1191 | 191.86
57528 | 3400 | 966 | 120.46 | 1000 | 131.62 | 1033 | 142.73 | 1065 | 153.72 | 1098 | 165.46 | 1130 | 177.1 | 1162 | 189.09 | 1194 | 201.43 | 1226 | 214.1 | 1260 | 228.02 | 1293 | 241.66
60912 | 3600 | 984 | 129.23 | 1016 | 140.53 | 1048 | 152.2 | 1080 | 164.22 | 1111 | 176.08 | 1141 | 187.76 | 1171 | 199.72 | 1202 | 212.52 | 1232 | 225.13 | 1262 | 238.07 | 1293 | 251.91
64296 | 3800 | 1004 | 138.78 | 1035 | 150.6 | 1065 | 162.33 | 1095 | 174.4 | 1125 | 186.79 | 1155 | 199.48 | 1184 | 211.93 | 1213 | 224.67 | 1241 | 237.13 | 1270 | 250.46 | 1299 | 264.11
67680 | 4000 | 1025 | 148.84 | 1054 | 160.67 | 1084 | 173.31 | 1113 | 185.84 | 1141 | 198.17 | 1170 | 211.34 | 1198 | 224.27 | 1226 | 237.46 | 1254 | 250.92 | 1281 | 264.05 | 1308 | 277.44
71064 | 4200 | 1047 | 159.5 | 1075 | 171.73 | 1104 | 184.8 | 1132 | 197.74 | 1159 | 210.46 | 1187 | 224.05 | 1214 | 237.38 | 1241 | 251 | 1268 | 264.89 | 1294 | 278.39 | 1320 | 292.13
77832 | 4600 | 1094 | 183 | 1121 | 196.44 | 1147 | 209.7 | 1173 | 223.31 | 1199 | 237.27 | 1224 | 250.93 | 1250 | 265.52 | 1275 | 279.77 | 1300 | 294.3 | 1325 | 309.12 | 1349 | 323.49
84600 | 5000 | 1145 | 209.85 | 1169 | 223.42 | 1194 | 237.84 | 1218 | 251.97 | 1242 | 266.39 | 1266 | 281.14 | 1290 | 296.22 | 1314 | 311.6 | 1337 | 326.56 | 1360 | 341.77 | 1384 | 358.02
High-pressure range
6000CEB
Outlet Area 20.70 ft² ¦ Wheel Dia. 60.00 in ¦ Tip Speed 15.71 × RPM (ft/min) ¦ Max BHP = 233.14 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 606 Class II — 780 Class III — 1050 Class IV — 1146
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
16560 | 800 | 199 | 1.77 | 261 | 3.41
18630 | 900 | 208 | 2.06 | 265 | 3.83
20700 | 1000 | 218 | 2.39 | 271 | 4.3 | 320 | 6.38
24840 | 1200 | 241 | 3.23 | 287 | 5.36 | 330 | 7.7 | 371 | 10.17
28980 | 1400 | 267 | 4.32 | 307 | 6.68 | 345 | 9.23 | 382 | 11.99 | 453 | 17.98
33120 | 1600 | 294 | 5.66 | 330 | 8.31 | 364 | 11.07 | 397 | 14.02 | 461 | 20.43 | 523 | 27.48
37260 | 1800 | 322 | 7.31 | 354 | 10.18 | 385 | 13.2 | 416 | 16.48 | 474 | 23.3 | 530 | 30.65 | 584 | 38.41
41400 | 2000 | 351 | 9.34 | 380 | 12.43 | 408 | 15.69 | 436 | 19.15 | 490 | 26.49 | 542 | 34.37 | 591 | 42.36 | 641 | 51.26
45540 | 2200 | 380 | 11.7 | 407 | 15.08 | 433 | 18.63 | 459 | 22.38 | 509 | 30.18 | 557 | 38.46 | 603 | 47.03 | 648 | 55.95 | 693 | 65.52 | 739 | 75.98
49680 | 2400 | 410 | 14.55 | 435 | 18.18 | 459 | 21.97 | 483 | 25.98 | 529 | 34.16 | 574 | 42.91 | 618 | 52.17 | 660 | 61.56 | 702 | 71.5 | 743 | 81.73 | 784 | 92.55
53820 | 2600 | 440 | 17.83 | 463 | 21.68 | 486 | 25.8 | 508 | 30.01 | 551 | 38.72 | 593 | 47.85 | 634 | 57.47 | 674 | 67.45 | 714 | 78.04 | 752 | 88.48 | 790 | 99.44
57960 | 2800 | 471 | 21.71 | 492 | 25.75 | 513 | 30.03 | 534 | 34.55 | 574 | 43.72 | 614 | 53.45 | 653 | 63.6 | 690 | 73.81 | 728 | 84.92 | 764 | 95.89 | 800 | 107.31
62100 | 3000 | 502 | 26.12 | 521 | 30.3 | 541 | 34.87 | 560 | 39.48 | 599 | 49.48 | 636 | 59.54 | 673 | 70.16 | 708 | 80.8 | 744 | 92.36 | 778 | 103.72 | 813 | 116
70380 | 3400 | 563 | 36.48 | 581 | 41.39 | 599 | 46.52 | 616 | 51.62 | 650 | 62.39 | 683 | 73.46 | 716 | 84.96 | 749 | 96.97 | 781 | 109.17 | 812 | 121.51 | 843 | 134.33
78660 | 3800 | 626 | 49.78 | 642 | 55.19 | 657 | 60.51 | 673 | 66.27 | 704 | 78.07 | 734 | 90.19 | 764 | 102.81 | 793 | 115.41 | 822 | 128.4 | 851 | 141.88 | 880 | 155.9
86940 | 4200 | 688 | 65.71 | 703 | 71.79 | 717 | 77.72 | 731 | 83.81 | 759 | 96.43 | 787 | 109.74 | 814 | 123.18 | 841 | 137.05 | 868 | 151.28 | 894 | 165.34 | 921 | 180.38
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
49680 | 2400 | 827 | 104.51
53820 | 2600 | 828 | 110.97 | 866 | 122.97
57960 | 2800 | 835 | 118.81 | 870 | 130.82 | 906 | 143.82 | 942 | 157.18
62100 | 3000 | 846 | 127.87 | 879 | 140.17 | 912 | 152.93 | 945 | 166.19 | 978 | 179.94 | 1012 | 194.52
66240 | 3200 | 859 | 137.43 | 891 | 150.49 | 922 | 163.47 | 952 | 176.31 | 983 | 190.13 | 1014 | 204.44 | 1045 | 219.18 | 1077 | 234.81
70380 | 3400 | 874 | 147.65 | 904 | 160.92 | 934 | 174.6 | 963 | 188.08 | 992 | 201.94 | 1021 | 216.21 | 1050 | 230.89 | 1079 | 246.03 | 1109 | 262.27 | 1139 | 278.77 | 1169 | 295.57
74520 | 3600 | 890 | 158.24 | 919 | 172.12 | 948 | 186.44 | 976 | 200.58 | 1004 | 215.06 | 1032 | 229.92 | 1059 | 244.48 | 1086 | 259.41 | 1114 | 275.46 | 1141 | 291.2 | 1169 | 308.11
78660 | 3800 | 908 | 169.89 | 936 | 184.33 | 963 | 198.62 | 990 | 213.29 | 1017 | 228.37 | 1044 | 243.8 | 1070 | 258.87 | 1097 | 275.02 | 1122 | 290.03 | 1148 | 306.16 | 1174 | 322.67
82800 | 4000 | 927 | 182.2 | 953 | 196.54 | 980 | 211.93 | 1006 | 227.1 | 1032 | 242.66 | 1058 | 258.62 | 1083 | 274.2 | 1109 | 290.87 | 1134 | 307.09 | 1158 | 322.81 | 1183 | 339.7
86940 | 4200 | 947 | 195.31 | 972 | 210.08 | 998 | 225.92 | 1023 | 241.52 | 1048 | 257.5 | 1073 | 273.88 | 1098 | 290.65 | 1122 | 306.98 | 1146 | 323.62 | 1170 | 340.56 | 1194 | 357.82
95220 | 4600 | 989 | 223.74 | 1013 | 239.88 | 1037 | 256.45 | 1061 | 273.48 | 1084 | 290.16 | 1107 | 307.2 | 1130 | 324.61 | 1153 | 342.4 | 1175 | 359.63 | 1198 | 378.11 | 1220 | 395.99
103500 | 5000 | 1035 | 256.49 | 1057 | 273.32 | 1080 | 291.28 | 1101 | 307.98 | 1123 | 325.88 | 1145 | 344.2 | 1167 | 362.93 | 1188 | 381.1 | 1209 | 399.59 | 1230 | 418.41 | 1251 | 437.57
High-pressure range
6600CEB
Outlet Area 25.04 ft² ¦ Wheel Dia. 66.00 in ¦ Tip Speed 17.28 × RPM (ft/min) ¦ Max BHP = 375.47 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 551 Class II — 710 Class III — 955 Class IV — 1040
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
20040 | 800 | 181 | 2.14 | 238 | 4.17
22545 | 900 | 189 | 2.49 | 241 | 4.64
25050 | 1000 | 198 | 2.89 | 246 | 5.18 | 291 | 7.73
30060 | 1200 | 219 | 3.9 | 261 | 6.5 | 300 | 9.31 | 338 | 12.39
35070 | 1400 | 243 | 5.24 | 279 | 8.08 | 314 | 11.2 | 347 | 14.47 | 412 | 21.78
40080 | 1600 | 267 | 6.83 | 300 | 10.06 | 331 | 13.41 | 361 | 16.98 | 419 | 24.71 | 475 | 33.15
45090 | 1800 | 293 | 8.87 | 322 | 12.34 | 350 | 15.98 | 378 | 19.91 | 431 | 28.22 | 481 | 36.9 | 531 | 46.51
50100 | 2000 | 319 | 11.29 | 346 | 15.12 | 371 | 19 | 397 | 23.28 | 445 | 31.96 | 492 | 41.41 | 538 | 51.46 | 583 | 62.12
55110 | 2200 | 346 | 14.23 | 370 | 18.24 | 394 | 22.6 | 417 | 27.02 | 462 | 36.34 | 506 | 46.44 | 548 | 56.85 | 589 | 67.67 | 630 | 79.28 | 672 | 92.02
60120 | 2400 | 373 | 17.64 | 395 | 21.92 | 417 | 26.53 | 439 | 31.42 | 481 | 41.36 | 522 | 51.97 | 561 | 62.86 | 600 | 74.5 | 638 | 86.45 | 675 | 98.7 | 713 | 112.13
65130 | 2600 | 400 | 21.57 | 421 | 26.24 | 442 | 31.26 | 462 | 36.36 | 501 | 46.87 | 539 | 57.87 | 576 | 69.41 | 613 | 81.73 | 649 | 94.39 | 684 | 107.24 | 718 | 120.24
70140 | 2800 | 428 | 26.23 | 447 | 31.1 | 467 | 36.48 | 485 | 41.69 | 522 | 52.96 | 558 | 64.61 | 593 | 76.71 | 628 | 89.62 | 661 | 102.38 | 695 | 116.26 | 727 | 129.71
75150 | 3000 | 456 | 31.52 | 474 | 36.75 | 492 | 42.24 | 510 | 48.03 | 544 | 59.69 | 578 | 71.97 | 611 | 84.56 | 644 | 97.93 | 676 | 111.57 | 708 | 125.9 | 739 | 140.32
85170 | 3400 | 512 | 44.18 | 528 | 50.03 | 544 | 56.12 | 560 | 62.45 | 591 | 75.52 | 621 | 88.92 | 651 | 102.84 | 681 | 117.38 | 710 | 132.1 | 738 | 146.92 | 767 | 162.95
95190 | 3800 | 569 | 60.2 | 583 | 66.56 | 598 | 73.48 | 612 | 80.26 | 640 | 94.46 | 667 | 109 | 694 | 124.11 | 721 | 139.69 | 748 | 155.82 | 774 | 171.91 | 800 | 188.64
105210 | 4200 | 626 | 79.72 | 639 | 86.82 | 652 | 94.12 | 665 | 101.61 | 690 | 116.68 | 715 | 132.52 | 740 | 149.05 | 765 | 166.13 | 789 | 182.98 | 813 | 200.26 | 837 | 218.05
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
60120 | 2400 | 752 | 126.56
65130 | 2600 | 752 | 133.9 | 788 | 149.22
70140 | 2800 | 759 | 143.72 | 791 | 158.35 | 823 | 173.63 | 856 | 189.97
75150 | 3000 | 769 | 154.68 | 799 | 169.55 | 829 | 185 | 859 | 201.04 | 889 | 217.67 | 920 | 235.39
80160 | 3200 | 781 | 166.36 | 810 | 182.11 | 838 | 197.68 | 866 | 213.75 | 894 | 230.36 | 922 | 247.53 | 950 | 265.23 | 979 | 284.06
85170 | 3400 | 794 | 178.29 | 822 | 194.85 | 849 | 211.2 | 876 | 228.02 | 902 | 244.51 | 929 | 262.32 | 955 | 279.8 | 981 | 297.8 | 1008 | 317.2 | 1035 | 336.9 | 1063 | 357.95
90180 | 3600 | 809 | 191.41 | 836 | 208.68 | 862 | 225.74 | 887 | 242.49 | 913 | 260.47 | 938 | 278.06 | 963 | 296.09 | 988 | 314.6 | 1013 | 333.6 | 1038 | 353.12 | 1063 | 373.12
95190 | 3800 | 825 | 205.23 | 851 | 223.12 | 876 | 240.78 | 900 | 258.1 | 925 | 276.74 | 949 | 294.93 | 973 | 313.51 | 997 | 332.52 | 1020 | 350.96 | 1044 | 370.86 | 1068 | 391.26
100200 | 4000 | 843 | 220.68 | 867 | 238.35 | 891 | 256.52 | 915 | 275.21 | 938 | 293.46 | 962 | 313.12 | 985 | 332.26 | 1008 | 351.78 | 1031 | 371.7 | 1053 | 390.93 | 1075 | 410.55
105210 | 4200 | 861 | 236.4 | 884 | 254.51 | 907 | 273.13 | 930 | 292.24 | 953 | 311.85 | 975 | 330.94 | 998 | 351.51 | 1020 | 371.47 | 1042 | 391.81 | 1064 | 412.52 | 1085 | 432.44
115230 | 4600 | 899 | 270.64 | 921 | 290.34 | 943 | 310.58 | 964 | 330.36 | 985 | 350.61 | 1006 | 371.32 | 1027 | 392.48 | 1048 | 414.1 | 1068 | 434.94 | 1089 | 457.42 | 1109 | 479.05
125250 | 5000 | 941 | 310.45 | 961 | 330.81 | 981 | 351.57 | 1001 | 372.76 | 1021 | 394.42 | 1041 | 416.59 | 1061 | 439.27 | 1080 | 461.14 | 1099 | 483.39 | 1118 | 506.05 | 1137 | 529.09
High-pressure range
7200CEB
Outlet Area 30.63 ft² ¦ Wheel Dia. 73.00 in ¦ Tip Speed 19.11 × RPM (ft/min) ¦ Max BHP = 621.54 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 498 Class II — 641 Class III — 863 Class IV — 940
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
24512 | 800 | 163 | 2.59 | 215 | 5.09
27576 | 900 | 171 | 3.05 | 218 | 5.69
30640 | 1000 | 179 | 3.53 | 223 | 6.38 | 263 | 9.44
36768 | 1200 | 198 | 4.77 | 236 | 7.95 | 271 | 11.36 | 305 | 15.07
42896 | 1400 | 219 | 6.35 | 252 | 9.85 | 284 | 13.72 | 314 | 17.75 | 372 | 26.54
49024 | 1600 | 242 | 8.42 | 271 | 12.27 | 299 | 16.36 | 326 | 20.7 | 379 | 30.27 | 430 | 40.71
55152 | 1800 | 265 | 10.87 | 291 | 15.07 | 317 | 19.65 | 342 | 24.41 | 389 | 34.34 | 435 | 45.17 | 480 | 56.86
61280 | 2000 | 288 | 13.75 | 312 | 18.35 | 336 | 23.37 | 359 | 28.5 | 403 | 39.29 | 445 | 50.71 | 486 | 62.79 | 527 | 75.95
67408 | 2200 | 313 | 17.44 | 335 | 22.42 | 356 | 27.6 | 377 | 33.06 | 418 | 44.56 | 457 | 56.63 | 496 | 69.78 | 533 | 83.01 | 570 | 97.19 | 607 | 112.25
73536 | 2400 | 337 | 21.54 | 357 | 26.79 | 377 | 32.46 | 397 | 38.46 | 435 | 50.64 | 472 | 63.6 | 508 | 77.25 | 543 | 91.4 | 577 | 105.85 | 610 | 120.57 | 644 | 136.76
79664 | 2600 | 362 | 26.47 | 381 | 32.2 | 399 | 38.07 | 417 | 44.26 | 453 | 57.36 | 487 | 70.66 | 521 | 85.02 | 554 | 99.86 | 586 | 115.01 | 618 | 130.92 | 649 | 146.98
85792 | 2800 | 387 | 32.1 | 404 | 38.01 | 422 | 44.56 | 439 | 51.18 | 472 | 64.81 | 505 | 79.28 | 536 | 93.77 | 567 | 109.18 | 598 | 125.48 | 628 | 141.98 | 657 | 158.46
91920 | 3000 | 412 | 38.49 | 429 | 45.1 | 445 | 51.74 | 461 | 58.72 | 492 | 73.1 | 523 | 88.27 | 553 | 103.78 | 582 | 119.65 | 611 | 136.37 | 640 | 153.93 | 668 | 171.54
104176 | 3400 | 463 | 54.09 | 478 | 61.45 | 492 | 68.73 | 506 | 76.27 | 534 | 92.22 | 562 | 109.1 | 589 | 126.09 | 615 | 143.11 | 642 | 161.67 | 667 | 179.54 | 693 | 198.95
116432 | 3800 | 514 | 73.46 | 527 | 81.39 | 540 | 89.57 | 553 | 98.02 | 578 | 115.18 | 603 | 133.32 | 628 | 152.23 | 652 | 171.01 | 676 | 190.39 | 700 | 210.51 | 723 | 230.49
128688 | 4200 | 566 | 97.54 | 578 | 106.37 | 589 | 114.87 | 601 | 124.17 | 624 | 142.86 | 647 | 162.55 | 669 | 182.31 | 691 | 202.67 | 713 | 223.53 | 735 | 244.96 | 757 | 267.03
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
73536 | 2400 | 680 | 154.88
79664 | 2600 | 680 | 163.87 | 712 | 182.2
85792 | 2800 | 686 | 175.64 | 715 | 193.58 | 744 | 212.32 | 774 | 232.44
91920 | 3000 | 695 | 189 | 722 | 207.08 | 749 | 225.84 | 776 | 245.32 | 804 | 266.51 | 832 | 288.16
98048 | 3200 | 706 | 203.41 | 732 | 222.47 | 758 | 242.15 | 783 | 261.51 | 808 | 281.5 | 833 | 302.15 | 859 | 324.54 | 885 | 347.32
104176 | 3400 | 718 | 218.23 | 743 | 238.19 | 768 | 258.78 | 792 | 278.93 | 816 | 299.64 | 839 | 319.83 | 863 | 341.76 | 887 | 364.36 | 911 | 387.57 | 936 | 412.42 | 961 | 437.75
110304 | 3600 | 732 | 234.71 | 755 | 254.43 | 779 | 275.79 | 802 | 296.69 | 825 | 318.11 | 848 | 340.07 | 871 | 362.62 | 893 | 384.49 | 915 | 406.92 | 938 | 431.31 | 961 | 456.32
116432 | 3800 | 746 | 251.17 | 769 | 272.53 | 792 | 294.55 | 814 | 316.08 | 836 | 338.17 | 858 | 360.78 | 880 | 383.9 | 901 | 406.23 | 923 | 430.44 | 944 | 453.81 | 965 | 477.73
122560 | 4000 | 762 | 269.79 | 784 | 291.73 | 805 | 313.15 | 827 | 336.35 | 848 | 358.92 | 869 | 382.05 | 890 | 405.7 | 911 | 429.84 | 932 | 454.49 | 952 | 478.17 | 972 | 502.33
128688 | 4200 | 778 | 288.71 | 799 | 311.08 | 820 | 334.09 | 841 | 357.73 | 861 | 380.68 | 882 | 405.53 | 902 | 429.57 | 922 | 454.13 | 942 | 479.17 | 962 | 504.67 | 981 | 529.05
140944 | 4600 | 813 | 331.35 | 833 | 355.6 | 852 | 379.17 | 872 | 404.75 | 891 | 429.57 | 910 | 454.94 | 929 | 480.88 | 947 | 505.76 | 966 | 532.75 | 984 | 558.58 | 1003 | 586.62
153200 | 5000 | 851 | 380.1 | 869 | 404.91 | 887 | 430.2 | 905 | 456 | 923 | 482.37 | 941 | 509.35 | 959 | 536.94 | 976 | 563.36 | 994 | 592.03 | 1011 | 619.43 | 1028 | 647.3
High-pressure range
8075CEB
Outlet Area 37.49 ft² ¦ Wheel Dia. 80.75 in ¦ Tip Speed 21.14 × RPM (ft/min) ¦ Max BHP = 1029.2 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 450 Class II — 579 Class III — 780 Class IV — 849
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
29992 | 800 | 148 | 3.21 | 194 | 6.19
33741 | 900 | 154 | 3.69 | 197 | 6.95
37490 | 1000 | 162 | 4.34 | 201 | 7.74 | 238 | 11.59
44988 | 1200 | 179 | 5.84 | 213 | 9.68 | 245 | 13.9 | 276 | 18.5
52486 | 1400 | 198 | 7.78 | 228 | 12.08 | 257 | 16.84 | 284 | 21.75 | 336 | 32.39
59984 | 1600 | 218 | 10.19 | 245 | 15.02 | 270 | 19.95 | 295 | 25.41 | 342 | 36.83 | 388 | 49.53
67482 | 1800 | 239 | 13.2 | 263 | 18.43 | 286 | 23.9 | 309 | 29.82 | 352 | 42.14 | 393 | 55.17 | 434 | 69.61
74980 | 2000 | 261 | 16.95 | 282 | 22.44 | 303 | 28.38 | 324 | 34.69 | 364 | 47.95 | 402 | 61.92 | 439 | 76.64 | 476 | 92.68
82478 | 2200 | 283 | 21.34 | 302 | 27.2 | 322 | 33.83 | 341 | 40.51 | 378 | 54.57 | 414 | 69.73 | 448 | 85.15 | 482 | 101.66 | 515 | 118.71 | 549 | 137.54
89976 | 2400 | 305 | 26.45 | 323 | 32.86 | 341 | 39.78 | 359 | 47.1 | 393 | 61.84 | 426 | 77.44 | 459 | 94.38 | 491 | 111.91 | 521 | 129.05 | 552 | 147.96 | 583 | 168.03
97474 | 2600 | 327 | 32.31 | 344 | 39.25 | 361 | 46.69 | 377 | 54.16 | 409 | 69.91 | 441 | 86.9 | 471 | 104.03 | 501 | 122.32 | 530 | 140.92 | 559 | 160.46 | 587 | 180.11
104972 | 2800 | 350 | 39.33 | 366 | 46.8 | 381 | 54.31 | 397 | 62.69 | 427 | 79.47 | 456 | 96.66 | 485 | 115.05 | 513 | 133.92 | 541 | 153.88 | 568 | 173.97 | 594 | 193.95
112470 | 3000 | 373 | 47.3 | 387 | 54.83 | 402 | 63.17 | 416 | 71.46 | 445 | 89.58 | 472 | 107.45 | 500 | 127.04 | 526 | 146.28 | 553 | 167.44 | 578 | 187.78 | 604 | 210.01
127466 | 3400 | 419 | 66.39 | 432 | 75.13 | 445 | 84.22 | 458 | 93.67 | 483 | 113.02 | 508 | 133.45 | 532 | 153.87 | 556 | 175.13 | 580 | 197.42 | 603 | 219.7 | 626 | 242.87
142462 | 3800 | 465 | 90.08 | 477 | 99.95 | 488 | 109.48 | 500 | 119.99 | 523 | 141.32 | 545 | 163.02 | 567 | 185.56 | 589 | 208.79 | 611 | 232.83 | 632 | 256.58 | 654 | 282.54
157458 | 4200 | 511 | 118.88 | 522 | 129.76 | 533 | 140.97 | 543 | 151.66 | 564 | 174.7 | 585 | 199 | 605 | 223.31 | 625 | 248.37 | 645 | 274.06 | 665 | 300.46 | 684 | 326.24
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
89976 | 2400 | 614 | 188.82
97474 | 2600 | 615 | 200.76 | 644 | 223.28
104972 | 2800 | 620 | 214.74 | 647 | 237.55 | 673 | 260.26 | 700 | 284.76
112470 | 3000 | 629 | 232.03 | 653 | 253.72 | 677 | 276.19 | 702 | 300.78 | 727 | 326.31 | 752 | 352.38
119968 | 3200 | 638 | 248.6 | 662 | 272.52 | 685 | 295.97 | 708 | 320.18 | 731 | 345.21 | 753 | 369.63 | 777 | 397.78 | 800 | 424.87
127466 | 3400 | 649 | 266.92 | 672 | 291.85 | 694 | 316.24 | 716 | 341.31 | 737 | 365.62 | 759 | 392.15 | 780 | 417.89 | 802 | 446.04 | 824 | 474.97 | 846 | 504.33 | 869 | 536.05
134964 | 3600 | 661 | 286.22 | 683 | 311.95 | 704 | 337.11 | 725 | 362.98 | 746 | 389.51 | 767 | 416.74 | 787 | 443.01 | 807 | 469.94 | 828 | 499.38 | 848 | 527.78 | 869 | 558.79
142462 | 3800 | 675 | 308.15 | 695 | 333.18 | 716 | 360.43 | 736 | 386.95 | 756 | 414.17 | 776 | 442.04 | 795 | 468.78 | 815 | 497.92 | 834 | 525.89 | 853 | 554.5 | 872 | 583.77
149960 | 4000 | 689 | 330.31 | 708 | 355.82 | 728 | 383.58 | 748 | 412.17 | 767 | 439.84 | 786 | 468.19 | 805 | 497.18 | 824 | 526.77 | 842 | 555.01 | 861 | 585.83 | 879 | 615.24
157458 | 4200 | 703 | 352.77 | 723 | 381.72 | 741 | 408.3 | 760 | 437.23 | 779 | 466.94 | 797 | 495.54 | 816 | 526.72 | 834 | 556.64 | 852 | 587.15 | 869 | 616.08 | 887 | 647.67
172454 | 4600 | 735 | 405.48 | 753 | 435.01 | 771 | 465.35 | 788 | 494.67 | 805 | 524.67 | 822 | 555.32 | 840 | 588.73 | 856 | 618.6 | 873 | 651.22 | 890 | 684.49 | 907 | 718.41
187450 | 5000 | 769 | 464.51 | 786 | 496.21 | 802 | 526.64 | 818 | 557.67 | 835 | 591.47 | 851 | 623.93 | 867 | 657.09 | 883 | 690.9 | 898 | 722.96 | 914 | 758.01 | 930 | 793.72
High-pressure range
BC SWSI 890
Outlet Area 45.54 ft² ¦ Wheel Dia. 89.00 in ¦ Tip Speed 23.30 × RPM (ft/min) ¦ Max BHP = 1662 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 408 Class II — 526 Class III — 708 Class IV — 770
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
36432 | 800 | 134 | 3.87 | 176 | 7.52
40986 | 900 | 140 | 4.51 | 179 | 8.48
45540 | 1000 | 147 | 5.27 | 183 | 9.5 | 216 | 14.08
54648 | 1200 | 163 | 7.17 | 193 | 11.71 | 223 | 17.05 | 250 | 22.36
63756 | 1400 | 180 | 9.5 | 207 | 14.71 | 233 | 20.41 | 258 | 26.52 | 305 | 39.4
72864 | 1600 | 198 | 12.42 | 222 | 18.17 | 245 | 24.25 | 268 | 30.98 | 311 | 45.05 | 352 | 60.15
81972 | 1800 | 217 | 16.07 | 239 | 22.49 | 260 | 29.2 | 280 | 36.08 | 319 | 51.01 | 357 | 67.25 | 394 | 84.7
91080 | 2000 | 237 | 20.64 | 256 | 27.3 | 275 | 34.51 | 294 | 42.16 | 330 | 58.11 | 365 | 75.38 | 399 | 93.59 | 432 | 112.68
100188 | 2200 | 256 | 25.7 | 274 | 33.04 | 292 | 41.03 | 309 | 49.03 | 343 | 66.32 | 375 | 84.28 | 407 | 103.84 | 437 | 123.22 | 467 | 143.96 | 498 | 166.96
109296 | 2400 | 277 | 32.22 | 293 | 39.9 | 309 | 48.14 | 325 | 56.84 | 357 | 75.39 | 387 | 94.43 | 416 | 114.27 | 445 | 135.5 | 473 | 157.06 | 501 | 179.92 | 529 | 204.16
118404 | 2600 | 297 | 39.37 | 312 | 47.63 | 327 | 56.44 | 342 | 65.76 | 371 | 84.87 | 400 | 105.46 | 427 | 126.07 | 455 | 149.02 | 481 | 171.32 | 507 | 194.71 | 532 | 218.06
127512 | 2800 | 317 | 47.52 | 332 | 56.82 | 346 | 66.16 | 360 | 76.03 | 387 | 96.22 | 414 | 117.65 | 440 | 139.72 | 465 | 162.22 | 491 | 187.09 | 515 | 210.9 | 539 | 235.68
136620 | 3000 | 338 | 57.25 | 352 | 67.11 | 365 | 76.91 | 378 | 87.19 | 403 | 108.21 | 429 | 131.22 | 453 | 153.66 | 478 | 178.55 | 501 | 202.51 | 525 | 228.87 | 548 | 255.1
154836 | 3400 | 380 | 80.55 | 392 | 91.3 | 403 | 101.74 | 415 | 113.34 | 438 | 137.08 | 461 | 162.2 | 483 | 187.28 | 505 | 213.43 | 526 | 239.5 | 547 | 266.73 | 568 | 295.07
173052 | 3800 | 422 | 109.51 | 432 | 120.75 | 443 | 133.21 | 454 | 146.1 | 474 | 171.11 | 495 | 198.66 | 515 | 226.15 | 535 | 254.49 | 554 | 282.28 | 574 | 312.64 | 593 | 342.56
191268 | 4200 | 464 | 144.75 | 474 | 158.02 | 483 | 170.62 | 493 | 184.61 | 512 | 212.58 | 530 | 240.69 | 549 | 271.39 | 567 | 301.61 | 585 | 332.56 | 603 | 364.34 | 621 | 397.08
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
109296 | 2400 | 557 | 229.27
118404 | 2600 | 558 | 243.89 | 584 | 270.8
127512 | 2800 | 563 | 261.52 | 587 | 288.52 | 611 | 316.74 | 635 | 345.72
136620 | 3000 | 570 | 280.83 | 593 | 309.03 | 615 | 336.74 | 637 | 365.5 | 659 | 395.29 | 682 | 427.5
145728 | 3200 | 579 | 302.21 | 600 | 330 | 621 | 358.66 | 642 | 388.27 | 663 | 418.89 | 684 | 450.58 | 705 | 483.25 | 726 | 516.44
154836 | 3400 | 589 | 324.5 | 609 | 353.29 | 630 | 384.76 | 649 | 413.4 | 669 | 444.77 | 689 | 477.1 | 708 | 508.28 | 728 | 542.59 | 747 | 575.54 | 768 | 613.63 | 788 | 650.05
163944 | 3600 | 600 | 348.16 | 620 | 379.51 | 639 | 410 | 658 | 441.35 | 677 | 473.48 | 696 | 506.44 | 714 | 538.04 | 732 | 570.41 | 751 | 606.02 | 769 | 640.14 | 788 | 677.63
173052 | 3800 | 612 | 373.54 | 631 | 405.55 | 649 | 436.56 | 668 | 470.52 | 686 | 503.29 | 704 | 536.81 | 722 | 571.1 | 739 | 603.74 | 757 | 639.61 | 774 | 673.76 | 792 | 711.37
182160 | 4000 | 625 | 401 | 643 | 433.51 | 661 | 466.99 | 678 | 499.22 | 696 | 534.53 | 713 | 568.4 | 730 | 603.02 | 747 | 638.31 | 764 | 674.34 | 781 | 711.12 | 797 | 745.91
191268 | 4200 | 638 | 428.87 | 656 | 463.74 | 673 | 497.51 | 690 | 532.17 | 707 | 567.72 | 723 | 601.67 | 740 | 638.9 | 756 | 674.34 | 773 | 713.18 | 789 | 749.96 | 805 | 787.41
209484 | 4600 | 667 | 492.86 | 683 | 527.98 | 699 | 564.01 | 715 | 601.02 | 731 | 638.98 | 746 | 675.12 | 762 | 714.79 | 777 | 752.46 | 792 | 790.85 | 807 | 829.95 | 823 | 872.93
227700 | 5000 | 698 | 564.96 | 713 | 602.43 | 728 | 640.65 | 743 | 679.7 | 757 | 716.79 | 772 | 757.59 | 786 | 796.29 | 801 | 838.82 | 815 | 879 | 829 | 919.89 | 843 | 961.47
High-pressure range
9825CEB
Outlet Area 55.50 ft² ¦ Wheel Dia. 98.25 in ¦ Tip Speed 25.72 × RPM (ft/min) ¦ Max BHP = 2744 × (RPM/1000)³ ¦ FEG85
MAXIMUM RPM: Class I — 370 Class II — 476 Class III — 641 Class IV — 698
CFM | OV | 0.5" SP |  | 1" SP |  | 1.5" SP |  | 2" SP |  | 3" SP |  | 4" SP |  | 5" SP |  | 6" SP |  | 7" SP |  | 8" SP |  | 9" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
44400 | 800 | 121 | 4.67 | 160 | 9.26
49950 | 900 | 127 | 5.52 | 162 | 10.3
55500 | 1000 | 133 | 6.4 | 165 | 11.42 | 196 | 17.25
66600 | 1200 | 147 | 8.62 | 175 | 14.32 | 202 | 20.78 | 227 | 27.44
77700 | 1400 | 163 | 11.57 | 187 | 17.78 | 211 | 24.85 | 233 | 32.02 | 277 | 48.39
88800 | 1600 | 179 | 15.04 | 201 | 22.11 | 222 | 29.57 | 243 | 37.86 | 281 | 54.48 | 319 | 73.4
99900 | 1800 | 197 | 19.72 | 216 | 27.22 | 235 | 35.35 | 254 | 44.16 | 289 | 62.19 | 323 | 81.67 | 357 | 103.31
111000 | 2000 | 214 | 24.91 | 232 | 33.32 | 249 | 42 | 266 | 51.19 | 299 | 70.86 | 331 | 92.16 | 361 | 113.65 | 391 | 136.98
122100 | 2200 | 232 | 31.36 | 249 | 40.65 | 264 | 49.71 | 280 | 59.81 | 311 | 81.05 | 340 | 102.99 | 368 | 125.85 | 396 | 150.33 | 423 | 175.41 | 451 | 203.32
133200 | 2400 | 250 | 38.83 | 266 | 48.94 | 280 | 58.73 | 295 | 69.69 | 323 | 91.55 | 350 | 114.53 | 377 | 139.44 | 403 | 165 | 428 | 190.78 | 453 | 218.06 | 479 | 248.5
144300 | 2600 | 269 | 47.96 | 283 | 58.28 | 297 | 69.33 | 310 | 80.3 | 336 | 103.36 | 362 | 128.16 | 387 | 153.88 | 412 | 181.39 | 436 | 209.2 | 459 | 236.87 | 482 | 265.9
155400 | 2800 | 288 | 58.43 | 301 | 69.42 | 313 | 80.3 | 326 | 92.56 | 351 | 117.7 | 375 | 143.35 | 399 | 170.82 | 422 | 198.79 | 444 | 226.82 | 467 | 257.83 | 488 | 286.77
166500 | 3000 | 306 | 69.64 | 318 | 81.12 | 330 | 93.18 | 342 | 105.88 | 365 | 131.81 | 388 | 159.16 | 411 | 188.15 | 433 | 217.6 | 454 | 247.06 | 475 | 277.91 | 496 | 310.12
188700 | 3400 | 344 | 97.97 | 355 | 111.17 | 365 | 123.92 | 376 | 138.2 | 397 | 167.35 | 417 | 196.82 | 437 | 227.41 | 457 | 259.32 | 477 | 292.83 | 496 | 326.04 | 515 | 360.59
210900 | 3800 | 382 | 133.17 | 392 | 147.92 | 401 | 161.98 | 411 | 177.71 | 430 | 209.44 | 448 | 241.45 | 466 | 274.69 | 484 | 308.92 | 502 | 344.33 | 520 | 381.1 | 537 | 417.08
233100 | 4200 | 420 | 176.01 | 429 | 192.07 | 438 | 208.6 | 446 | 224.1 | 464 | 259.4 | 481 | 294.96 | 497 | 330.11 | 514 | 368.38 | 530 | 405.46 | 546 | 443.46 | 562 | 482.53
Low-pressure range
CFM | OV | 10" SP |  | 11" SP |  | 12" SP |  | 13" SP |  | 14" SP |  | 15" SP |  | 16" SP |  | 17" SP |  | 18" SP |  | 19" SP |  | 20" SP
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
133200 | 2400 | 505 | 280.14
144300 | 2600 | 505 | 296.4 | 529 | 329.99
155400 | 2800 | 510 | 318.72 | 531 | 350.16 | 553 | 385.02 | 575 | 420.86
166500 | 3000 | 517 | 343.57 | 537 | 376.26 | 557 | 410.16 | 577 | 445.37 | 597 | 481.84 | 618 | 521.52
177600 | 3200 | 525 | 369.38 | 544 | 403.25 | 563 | 438.18 | 582 | 474.26 | 600 | 509.02 | 619 | 547.52 | 638 | 587.2 | 658 | 630.4
188700 | 3400 | 534 | 396.47 | 552 | 431.33 | 570 | 467.21 | 588 | 504.06 | 606 | 541.99 | 624 | 581.07 | 641 | 618.45 | 659 | 659.87 | 677 | 702.43 | 695 | 745.6 | 714 | 792.84
199800 | 3600 | 544 | 425.44 | 561 | 460.96 | 579 | 500.08 | 596 | 537.73 | 613 | 576.28 | 630 | 615.81 | 647 | 656.37 | 663 | 694.89 | 680 | 737.59 | 697 | 781.47 | 714 | 826.48
210900 | 3800 | 554 | 454.29 | 571 | 492.7 | 588 | 532.31 | 605 | 573.11 | 621 | 612.12 | 638 | 655.07 | 654 | 695.91 | 670 | 737.67 | 685 | 776.99 | 701 | 820.65 | 717 | 865.36
222000 | 4000 | 566 | 488.27 | 582 | 527.05 | 598 | 566.92 | 614 | 607.89 | 630 | 649.95 | 646 | 693.11 | 662 | 737.31 | 677 | 779.04 | 692 | 821.55 | 707 | 864.91 | 722 | 909.16
233100 | 4200 | 578 | 522.83 | 594 | 564.47 | 609 | 604.4 | 625 | 648.42 | 640 | 690.45 | 655 | 733.47 | 670 | 777.46 | 685 | 822.43 | 700 | 868.3 | 715 | 915.05 | 729 | 958.78
255300 | 4600 | 604 | 600.02 | 619 | 644.38 | 633 | 686.72 | 648 | 733.52 | 662 | 778.08 | 676 | 823.61 | 690 | 870.12 | 704 | 917.61 | 718 | 966.07 | 731 | 1011.34 | 745 | 1061.62
277500 | 5000 | 632 | 687.57 | 646 | 734.6 | 659 | 779.11 | 673 | 828.15 | 686 | 874.57 | 699 | 921.99 | 712 | 970.41 | 725 | 1019.76 | 738 | 1070.05 | 751 | 1121.26 | 764 | 1173.41
High-pressure range