## 1200PRVDD
1200PRVDD— 12" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750 Max Motor Frame Size = 56
1200PRVDD | 16 | 1/4 | 1750 | 0.21 | 14.3 | 1584 | 1517 | 1499 | 1480 | 1441 | 1398
1200PRVDD | 20 | 1/4 | 1750 | 0.26 | 14.2 | 1838 | 1764 | 1745 | 1724 | 1682 | 1637 | 1588 | 1508
1200PRVDD | 24 | 1/3 | 1750 | 0.32 | 14.3 | 2095 | 2016 | 1996 | 1974 | 1930 | 1883 | 1832 | 1749 | 1596 | 1413
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 1600PRVDD
1600PRVDD— 16" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750 Max Motor Frame Size = 56
1600PRVDD | 16 | 1/3 | 1750 | 0.34 | 13.4 | 2272 | 2191 | 2170 | 2148 | 2103 | 2056 | 2005 | 1923
1600PRVDD | 20 | 1/2 | 1750 | 0.44 | 15 | 2668 | 2574 | 2551 | 2526 | 2478 | 2428 | 2379 | 2305 | 2167 | 1959
1600PRVDD | 24 | 1/2 | 1750 | 0.55 | 15.4 | 3051 | 2965 | 2943 | 2920 | 2873 | 2822 | 2769 | 2681 | 2508 | 2304 | 2046
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 1800PRVDD
1800PRVDD — 18" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750 Max Motor Frame Size = 56
1800PRVDD | 12 | 1/2 | 1750 | 0.43 | 23 | 2565 | 2457 | 2430 | 2402 | 2346 | 2288
1800PRVDD | 16 | 1/2 | 1750 | 0.52 | 22 | 3135 | 3037 | 3012 | 2986 | 2934 | 2880 | 2824 | 2738 | 2580 | 2379
1800PRVDD | 20 | 3/4 | 1750 | 0.68 | 23 | 3713 | 3597 | 3568 | 3539 | 3482 | 3426 | 3370 | 3292 | 3166 | 3017 | 2683
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 2000PRVDD
2000PRVDD — 20" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750 Max Motor Frame Size = 145T
2000PRVDD | 12 | 3/4 | 1750 | 0.68 | 22 | 3745 | 3613 | 3579 | 3544 | 3473 | 3399 | 3322 | 3199
2000PRVDD | 16 | 1 | 1750 | 0.88 | 23 | 4678 | 4540 | 4505 | 4470 | 4398 | 4326 | 4251 | 4140 | 3947 | 3723 | 3428
2000PRVDD | 20 | 1 1/2 | 1750 | 1.16 | 26 | 5591 | 5450 | 5415 | 5379 | 5307 | 5234 | 5161 | 5050 | 4871 | 4684 | 4445 | 3635
2000PRVDD | 24 | 1 1/2 | 1750 | 1.46 | 28 | 6442 | 6315 | 6282 | 6249 | 6181 | 6111 | 6038 | 5925 | 5721 | 5491 | 5228 | 4503
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 2400PRVDD
2400PRVDD — 24" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750, Z5 = 1750 Max Motor Frame Size = 184T
2400PRVDD | 30 | 1/4 | 860 | 0.23 | 13.4 | 4379
2400PRVDD | 35 | 1/3 | 860 | 0.32 | 13.6 | 5198 | 4770 | 4644 | 4506 | 4190
2400PRVDD | 40 | 1/2 | 860 | 0.42 | 14.7 | 5993 | 5503 | 5351 | 5180 | 4826 | 4484
2400PRVDD | 45 | 1/2 | 860 | 0.51 | 15.4 | 6504 | 5960 | 5802 | 5633 | 5255 | 4798
2400PRVDD | 30 | 1/2 | 1160 | 0.56 | 23 | 5906 | 5574 | 5491 | 5409 | 5249 | 5093 | 4926 | 4606
2400PRVDD | 35 | 3/4 | 1160 | 0.79 | 23 | 7011 | 6710 | 6629 | 6545 | 6368 | 6174 | 5959 | 5593 | 4767
2400PRVDD | 40 | 1 | 1160 | 1.03 | 25 | 8084 | 7741 | 7648 | 7551 | 7344 | 7106 | 6842 | 6454 | 5765
2400PRVDD | 45 | 1 1/2 | 1160 | 1.24 | 26 | 8774 | 8388 | 8285 | 8179 | 7956 | 7715 | 7454 | 7022
2400PRVDD | 30 | 2 | 1750 | 1.92 | 44 | 8910 | 8690 | 8635 | 8580 | 8470 | 8360 | 8250 | 8087 | 7827 | 7563 | 7263 | 6374
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 3000PRVDD
3000PRVDD — 30" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750, Z5 = 1160 Max Motor Frame Size = 184T
3000PRVDD | 30 | 1/2 | 860 | 0.46 | 18.2 | 7675 | 6925 | 6767 | 6612 | 6273
3000PRVDD | 35 | 3/4 | 860 | 0.66 | 18.4 | 9036 | 8385 | 8218 | 8054 | 7718 | 7325 | 6770
3000PRVDD | 40 | 1 | 860 | 0.89 | 18.8 | 10518 | 9780 | 9583 | 9380 | 8953 | 8488 | 7977 | 6878
3000PRVDD | 45 | 1 | 860 | 1.09 | 19.3 | 11378 | 10592 | 10383 | 10170 | 9724 | 9250 | 8771
3000PRVDD | 30 | 1 1/2 | 1160 | 1.14 | 28 | 10352 | 9767 | 9630 | 9498 | 9255 | 9024 | 8791 | 8398 | 7587 | 6331
3000PRVDD | 35 | 1 1/2 | 1160 | 1.61 | 28 | 12188 | 11711 | 11590 | 11467 | 11220 | 10974 | 10731 | 10352 | 9541 | 8396
3000PRVDD | 40 | 2 | 1160 | 2.18 | 30 | 14188 | 13653 | 13514 | 13374 | 13086 | 12791 | 12485 | 12003 | 11118 | 10018
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 3600PRVDD
3600PRVDD — 36" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1750, E8 = 1750, Z5 = 1160 Max Motor Frame Size = 215T
3600PRVDD | 30 | 1 1/2 | 860 | 1.15 | 26 | 13261 | 12327 | 12115 | 11918 | 11544 | 11162 | 10728 | 9962
3600PRVDD | 35 | 1 1/2 | 860 | 1.63 | 26 | 15612 | 14837 | 14639 | 14438 | 14040 | 13646 | 13232 | 12483 | 10674
3600PRVDD | 40 | 2 | 860 | 2.21 | 26 | 18173 | 17301 | 17073 | 16840 | 16363 | 15865 | 15340 | 14488 | 12734
3600PRVDD | 45 | 3 | 860 | 2.71 | 27 | 19657 | 18727 | 18485 | 18239 | 17735 | 17212 | 16666 | 15812 | 14092
3600PRVDD | 30 | 3 | 1160 | 2.83 | 40 | 17886 | 17171 | 17002 | 16835 | 16511 | 16208 | 15923 | 15509 | 14779 | 13896 | 12828
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 4200PRVDD
4200PRVDD — 42" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1160, E8 = 1160, Z5 = 860 Max Motor Frame Size = 256T
4200PRVDD | 30 | 3 | 860 | 3.2 | 33 | 21735 | 21160 | 21008 | 20852 | 20527 | 20183 | 19814 | 19179 | 17864 | 16492 | 14712
4200PRVDD | 35 | 5 | 860 | 4.38 | 36 | 26204 | 25057 | 24802 | 24558 | 24118 | 23728 | 23360 | 22814 | 21774 | 20214 | 18311
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 4800PRVDD
4200PRVDD — 48" Wheel
Direct Drive — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Max RPM: E4 = 1160, E8 = 1160, Z5 = 860 Max Motor Frame Size = 256T
4200PRVDD | 30 | 5 | 860 | 4.86 | 44 | 31423 | 30140 | 29835 | 29537 | 28956 | 28417 | 27909 | 27164 | 25831 | 24215 | 22225
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 2000PRV
2000PRV — 20" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM E4 = 1890, E8 = 1280 ¦ Max Motor Frame Size = 145T
2000PRV | 32 | 1/4 | 885 | 0.27 | 11.6 | 4063 | 3727 | 3640 | 3552 | 3360 | 3097
2000PRV | 32 | 1/3 | 974 | 0.37 | 13.4 | 4472 | 4169 | 4090 | 4011 | 3849 | 3667 | 3425
2000PRV | 32 | 1/2 | 1113 | 0.55 | 16.1 | 5110 | 4847 | 4779 | 4710 | 4572 | 4431 | 4280 | 3993 | 3334
2000PRV | 32 | 3/4 | 1277 | 0.82 | 20 | 5863 | 5635 | 5577 | 5518 | 5398 | 5277 | 5156 | 4965 | 4556 | 3989
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 2400PRV
2400PRV— 24" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM E4 = 1930, E8 = 1175, Z5 = 1450 ¦ Max Motor Frame Size = 145T
2400PRV | 30 | 1/3 | 1003 | 0.37 | 17.8 | 5127 | 4721 | 4625 | 4533 | 4349 | 4135
2400PRV | 45 | 1/3 | 766 | 0.37 | 13.6 | 5668 | 5057 | 4900 | 4720 | 4126
2400PRV | 30 | 1/2 | 1146 | 0.55 | 22 | 5858 | 5500 | 5413 | 5327 | 5166 | 5006 | 4832 | 4496
2400PRV | 45 | 1/2 | 875 | 0.55 | 17.4 | 6474 | 5940 | 5806 | 5671 | 5361 | 4857
2400PRV | 30 | 3/4 | 1310 | 0.82 | 27 | 6697 | 6382 | 6305 | 6228 | 6078 | 5937 | 5798 | 5578 | 5093 | 4305
2400PRV | 45 | 3/4 | 1001 | 0.82 | 22 | 7407 | 6943 | 6823 | 6706 | 6469 | 6205 | 5838 | 4994
2400PRV | 30 | 1 | 1446 | 1.1 | 31 | 7392 | 7106 | 7035 | 6966 | 6827 | 6692 | 6565 | 6376 | 6027 | 5554 | 4844
2400PRV | 45 | 1 | 1104 | 1.1 | 25 | 8169 | 7750 | 7642 | 7534 | 7322 | 7105 | 6866 | 6351
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 3000PRV
3000PRV — 30" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM E4 = 1565, E8 = 975, Z5 = 1295 ¦ Max Motor Frame Size = 184T
3000PRV | 35 | 1/2 | 813 | 0.55 | 17.7 | 8369 | 7720 | 7535 | 7336 | 6897 | 6412
3000PRV | 45 | 1/2 | 680 | 0.55 | 14.2 | 8904 | 7908 | 7645 | 7359 | 6706
3000PRV | 35 | 3/4 | 929 | 0.82 | 22 | 9563 | 9008 | 8856 | 8697 | 8352 | 7970 | 7559 | 6851
3000PRV | 45 | 3/4 | 778 | 0.82 | 17.9 | 10187 | 9322 | 9101 | 8874 | 8381 | 7826
3000PRV | 35 | 1 | 1025 | 1.1 | 26 | 10552 | 10054 | 9921 | 9783 | 9492 | 9172 | 8825 | 8264 | 7106
3000PRV | 45 | 1 | 858 | 1.1 | 21 | 11235 | 10454 | 10253 | 10053 | 9638 | 9178 | 8675
3000PRV | 35 | 1 1/2 | 1174 | 1.65 | 32 | 12085 | 11657 | 11544 | 11429 | 11190 | 10937 | 10666 | 10223 | 9410 | 8429
3000PRV | 45 | 1 1/2 | 983 | 1.65 | 26 | 12871 | 12194 | 12020 | 11845 | 11495 | 11136 | 10750 | 10112
3000PRV | 35 | 2 | 1293 | 2.2 | 38 | 13310 | 12924 | 12824 | 12721 | 12510 | 12291 | 12061 | 11690 | 11003 | 10246 | 9349
3000PRV | 45 | 2 | 1082 | 2.2 | 30 | 14168 | 13555 | 13398 | 13240 | 12923 | 12604 | 12276 | 11746 | 10732
3000PRV | 45 | 3 | 1239 | 3.3 | 38 | 16223 | 15691 | 15555 | 15419 | 15143 | 14865 | 14588 | 14164 | 13396 | 12532
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 3600PRV
3600PRV— 36" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM E4 = 1395, E8 = 915, Z5 = 1095 ¦ Max Motor Frame Size = 184T
3600PRV | 35 | 3/4 | 686 | 0.82 | 18.8 | 12201 | 11280 | 11019 | 10738 | 10120 | 9440
3600PRV | 45 | 3/4 | 574 | 0.82 | 15.2 | 12984 | 11571 | 11200 | 10800 | 9892
3600PRV | 35 | 1 | 757 | 1.1 | 22 | 13464 | 12643 | 12418 | 12181 | 11664 | 11091 | 10474 | 9377
3600PRV | 45 | 1 | 634 | 1.1 | 17.9 | 14342 | 13067 | 12740 | 12405 | 11663 | 10808
3600PRV | 35 | 1 1/2 | 867 | 1.65 | 27 | 15421 | 14716 | 14528 | 14334 | 13923 | 13475 | 12989 | 12202 | 10619
3600PRV | 45 | 1 1/2 | 726 | 1.65 | 22 | 16423 | 15317 | 15033 | 14749 | 14165 | 13523 | 12823
3600PRV | 35 | 2 | 954 | 2.2 | 32 | 16968 | 16334 | 16167 | 15995 | 15639 | 15259 | 14850 | 14184 | 12954 | 11409
3600PRV | 45 | 2 | 799 | 2.2 | 26 | 18074 | 17074 | 16816 | 16559 | 16041 | 15504 | 14917 | 13952
3600PRV | 35 | 3 | 1093 | 3.3 | 40 | 19440 | 18893 | 18750 | 18605 | 18307 | 17997 | 17673 | 17152 | 16187 | 15127 | 13898
3600PRV | 45 | 3 | 915 | 3.3 | 32 | 20698 | 19829 | 19607 | 19384 | 18933 | 18482 | 18020 | 17280 | 15874
3600PRV | 45 | 5 | 1085 | 5.5 | 44 | 24544 | 23815 | 23630 | 23443 | 23068 | 22688 | 22308 | 21735 | 20728 | 19597
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 4200PRV
4200PRV — 42" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM E4 = 965, E8 = 660, Z5 = 870 ¦ Max Motor Frame Size = 215T
4200PRV | 30 | 1 | 602 | 1.1 | 21 | 15457 | 14311 | 14018 | 13726 | 13133 | 12479
4200PRV | 45 | 1 | 466 | 1.1 | 19.8 | 17433 | 15556 | 15031 | 14446 | 12882
4200PRV | 30 | 1 1/2 | 690 | 1.65 | 25 | 17716 | 16722 | 16468 | 16212 | 15703 | 15187 | 14641 | 13706
4200PRV | 45 | 1 1/2 | 534 | 1.65 | 24 | 19977 | 18370 | 17938 | 17489 | 16486 | 15166 | 13374
4200PRV | 30 | 2 | 759 | 2.2 | 29 | 19488 | 18587 | 18357 | 18127 | 17661 | 17199 | 16730 | 15979 | 14482 | 12216
4200PRV | 45 | 2 | 588 | 2.2 | 28 | 21997 | 20555 | 20169 | 19776 | 18949 | 17997 | 16786 | 14241
4200PRV | 30 | 3 | 869 | 3.3 | 35 | 22312 | 21528 | 21329 | 21129 | 20726 | 20320 | 19915 | 19306 | 18215 | 16932 | 15286
4200PRV | 45 | 3 | 673 | 3.3 | 34 | 25177 | 23933 | 23606 | 23271 | 22587 | 21869 | 21083 | 19630 | 15910
4200PRV | 40 | 5 | 848 | 5.49 | 44 | 29298 | 28363 | 28125 | 27885 | 27400 | 26908 | 26421 | 25684 | 24344 | 22583 | 20228
4200PRV | 45 | 5 | 798 | 5.5 | 44 | 29853 | 28817 | 28548 | 28276 | 27717 | 27145 | 26559 | 25630 | 23771 | 21168
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 4800PRV
4800PRV — 48" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM E4 = 1025, E8 = 670, Z5 = 805 ¦ Max Motor Frame Size = 215T
4800PRV | 35 | 1 1/2 | 537 | 1.65 | 22 | 22635 | 21078 | 20644 | 20181 | 19164 | 18046 | 16800
4800PRV | 45 | 1 1/2 | 449 | 1.65 | 17.9 | 24067 | 21663 | 21040 | 20385 | 18916
4800PRV | 35 | 2 | 591 | 2.2 | 25 | 24911 | 23517 | 23137 | 22742 | 21886 | 20939 | 19920 | 18198
4800PRV | 45 | 2 | 495 | 2.2 | 21 | 26532 | 24360 | 23805 | 23240 | 22023 | 20655
4800PRV | 35 | 3 | 676 | 3.29 | 32 | 28494 | 27294 | 26975 | 26647 | 25960 | 25216 | 24411 | 23104 | 20602
4800PRV | 45 | 3 | 566 | 3.3 | 26 | 30338 | 28451 | 27965 | 27481 | 26496 | 25442 | 24279 | 22145
4800PRV | 35 | 5 | 802 | 5.5 | 42 | 33805 | 32808 | 32548 | 32283 | 31738 | 31170 | 30574 | 29610 | 27829 | 25860 | 23502
4800PRV | 45 | 5 | 671 | 5.49 | 33 | 35966 | 34386 | 33982 | 33574 | 32756 | 31933 | 31086 | 29706 | 27045
4800PRV | 45 | 7 1/2 | 768 | 8.23 | 42 | 41165 | 39791 | 39441 | 39089 | 38378 | 37662 | 36947 | 35851 | 33849 | 31594
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 5400PRV
5400PRV — 54" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM C3 = 985, C6 = 795, Z5 = 665 ¦ Max Motor Frame Size = 254T
5400PRV | 30 | 1 1/2 | 444 | 1.65 | 18.8 | 24869 | 22842 | 22342 | 21853 | 20846
5400PRV | 45 | 1 1/2 | 341 | 1.65 | 17.1 | 27747 | 24529 | 23637 | 22577
5400PRV | 30 | 2 | 489 | 2.2 | 22 | 27390 | 25550 | 25088 | 24635 | 23746 | 22814 | 21732
5400PRV | 45 | 2 | 375 | 2.19 | 19.7 | 30514 | 27613 | 26849 | 26034 | 23927 | 20730
5400PRV | 30 | 3 | 559 | 3.29 | 27 | 31310 | 29702 | 29299 | 28895 | 28100 | 27323 | 26528 | 25185 | 22250
5400PRV | 45 | 3 | 430 | 3.3 | 25 | 34989 | 32487 | 31833 | 31173 | 29769 | 28008 | 25497
5400PRV | 30 | 5 | 663 | 5.5 | 35 | 37136 | 35781 | 35441 | 35102 | 34421 | 33743 | 33083 | 32098 | 30319 | 28105 | 25103
5400PRV | 45 | 5 | 510 | 5.51 | 33 | 41499 | 39419 | 38876 | 38325 | 37219 | 36076 | 34817 | 32339
5400PRV | 40 | 7 1/2 | 622 | 8.25 | 41 | 46963 | 45450 | 45056 | 44657 | 43837 | 42988 | 42111 | 40726 | 38118 | 34825 | 30510
5400PRV | 45 | 7 1/2 | 584 | 8.27 | 41 | 47520 | 45718 | 45253 | 44782 | 43822 | 42858 | 41876 | 40294 | 36736 | 31312
5400PRV | 45 | 10 | 643 | 11.04 | 48 | 52321 | 50691 | 50273 | 49851 | 48992 | 48117 | 47242 | 45899 | 43382 | 39808 | 34855
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.

## 6000PRV
6000PRV — 60" Wheel
Belt Driven (Standard) — Low Profile Upblast Propeller Roof Ventilator • Body values = CFM at each static pressure (in. w.g.), standard air density
Propeller | Blade Angle | Motor HP | Fan RPM | Max BHP | Sones @ 0" SP | STATIC PRESSURE (IN. W.G.)
[6 empty] | 0.000 | 0.100 | 0.125 | 0.150 | 0.200 | 0.250 | 0.300 | 0.375 | 0.500 | 0.625 | 0.750 | 1.000
Level 3 Performance ¦ Max RPM C3 = 955, C6 = 850, Z5 = 685 ¦ Max Motor Frame Size = 256T
6000PRV | 30 | 1 1/2 | 398 | 1.65 | 17.9 | 28796 | 26269 | 25554 | 24794
6000PRV | 45 | 1 1/2 | 303 | 1.66 | 15.6 | 32335 | 27976 | 26696 | 25211
6000PRV | 30 | 2 | 438 | 2.2 | 20 | 31690 | 29430 | 28811 | 28160 | 26756 | 25251
6000PRV | 45 | 2 | 333 | 2.2 | 18.1 | 35536 | 31623 | 30561 | 29389 | 26497
6000PRV | 30 | 3 | 502 | 3.31 | 26 | 36321 | 34382 | 33865 | 33332 | 32205 | 30988 | 29696 | 27658
6000PRV | 45 | 3 | 381 | 3.29 | 23 | 40658 | 37279 | 36394 | 35482 | 33464 | 31014
6000PRV | 30 | 5 | 595 | 5.51 | 33 | 43049 | 41438 | 41017 | 40587 | 39702 | 38773 | 37791 | 36219 | 33416 | 30110
6000PRV | 45 | 5 | 452 | 5.5 | 30 | 48235 | 45427 | 44692 | 43952 | 42441 | 40827 | 38992 | 35612
6000PRV | 40 | 7 1/2 | 553 | 8.25 | 37 | 54361 | 52204 | 51655 | 51102 | 49987 | 48886 | 47780 | 46035 | 42391 | 37248
6000PRV | 45 | 7 1/2 | 517 | 8.23 | 37 | 55172 | 52737 | 52107 | 51469 | 50175 | 48858 | 47484 | 45187 | 40258
6000PRV | 35 | 10 | 672 | 11 | 45 | 56980 | 55560 | 55193 | 54820 | 54059 | 53272 | 52459 | 51177 | 48837 | 46249 | 43363 | 36164
6000PRV | 40 | 10 | 609 | 11.02 | 43 | 59866 | 57912 | 57416 | 56918 | 55912 | 54900 | 53900 | 52391 | 49644 | 46087 | 41376
6000PRV | 45 | 10 | 570 | 11.03 | 42 | 60827 | 58630 | 58065 | 57494 | 56331 | 55155 | 53961 | 52084 | 48450 | 43501
Note: Performance for installation Type A (free inlet, free outlet) at standard air density. BHP excludes drive (transmission) losses. Sones are loudness @ 0" SP per AMCA Standard 301. CFM values read left-to-right from 0.000" SP; blank cells indicate the selection is past its useful range.