## 0900DIDWCFAB
0900DIDWCFAB · 9" Wheel Diameter · Class L/R max 2800 RPM
Outlet velocity OV (FPM) = 1.1198 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | .5" |  | .75" |  | 1" |  | 1.25" |  | 1.5" |  | 1.75" |  | 2" |  | 2.5" |  | 3"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1800 | 2016 | 1029 | 0.53 | 1167 | 0.64 | 1292 | 0.76
1900 | 2128 | 1056 | 0.6 | 1188 | 0.71 | 1312 | 0.84
2000 | 2240 | 1085 | 0.67 | 1210 | 0.79 | 1332 | 0.92 | 1442 | 1.05
2100 | 2352 | 1115 | 0.75 | 1233 | 0.87 | 1352 | 1.01 | 1461 | 1.15
2200 | 2464 | 1146 | 0.84 | 1259 | 0.97 | 1373 | 1.11 | 1482 | 1.25 | 1581 | 1.39
2300 | 2576 | 1177 | 0.94 | 1286 | 1.07 | 1395 | 1.21 | 1502 | 1.36 | 1601 | 1.51
2400 | 2688 | 1209 | 1.04 | 1314 | 1.17 | 1418 | 1.32 | 1523 | 1.48 | 1621 | 1.63 | 1712 | 1.79
2600 | 2911 | 1275 | 1.27 | 1374 | 1.42 | 1470 | 1.57 | 1566 | 1.73 | 1662 | 1.9 | 1753 | 2.07 | 1837 | 2.24
2800 | 3135 | 1344 | 1.54 | 1436 | 1.69 | 1526 | 1.85 | 1615 | 2.02 | 1705 | 2.2 | 1794 | 2.38 | 1878 | 2.56 | 2033 | 2.92
3000 | 3359 | 1414 | 1.84 | 1501 | 2.01 | 1586 | 2.18 | 1669 | 2.35 | 1752 | 2.53 | 1836 | 2.72 | 1919 | 2.92 | 2073 | 3.31
3200 | 3583 | 1485 | 2.19 | 1567 | 2.36 | 1648 | 2.54 | 1727 | 2.73 | 1804 | 2.91 | 1882 | 3.1 | 1961 | 3.31 | 2114 | 3.73 | 2253 | 4.14
3400 | 3807 | 1556 | 2.57 | 1636 | 2.76 | 1712 | 2.95 | 1787 | 3.14 | 1861 | 3.34 | 1933 | 3.53 | 2007 | 3.74 | 2155 | 4.19 | 2294 | 4.63
3600 | 4031 | 1629 | 3 | 1705 | 3.21 | 1778 | 3.41 | 1850 | 3.61 | 1920 | 3.81 | 1989 | 4.02 | 2058 | 4.23 | 2197 | 4.68
3800 | 4255 | 1702 | 3.48 | 1776 | 3.7 | 1845 | 3.91 | 1914 | 4.12 | 1981 | 4.33 | 2047 | 4.55 | 2112 | 4.77
4000 | 4479 | 1775 | 4.01 | 1847 | 4.24 | 1914 | 4.46 | 1979 | 4.68 | 2044 | 4.91
4200 | 4703 | 1849 | 4.58 | 1919 | 4.83
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 1050DIDWCFAB
1050DIDWCFAB · 10.5" Wheel Diameter · Class L/R max 2400 RPM
Outlet velocity OV (FPM) = 0.896 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | .25" |  | .5" |  | .75" |  | 1" |  | 1.25" |  | 1.5" |  | 1.75" |  | 2" |  | 2.5"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2000 | 1792 | 749 | 0.41 | 888 | 0.52 | 1019 | 0.66
2200 | 1971 | 796 | 0.51 | 923 | 0.64 | 1049 | 0.78 | 1161 | 0.92
2400 | 2150 | 846 | 0.64 | 964 | 0.78 | 1079 | 0.92 | 1190 | 1.08
2600 | 2330 | 897 | 0.79 | 1007 | 0.94 | 1113 | 1.09 | 1220 | 1.26 | 1318 | 1.43
2800 | 2509 | 949 | 0.96 | 1052 | 1.12 | 1151 | 1.28 | 1251 | 1.45 | 1348 | 1.64 | 1437 | 1.82
3000 | 2688 | 1001 | 1.16 | 1099 | 1.33 | 1193 | 1.5 | 1285 | 1.67 | 1378 | 1.87 | 1467 | 2.07 | 1549 | 2.26
3200 | 2867 | 1054 | 1.38 | 1148 | 1.56 | 1237 | 1.74 | 1323 | 1.92 | 1410 | 2.12 | 1497 | 2.34 | 1578 | 2.54 | 1655 | 2.75
3400 | 3046 | 1108 | 1.63 | 1198 | 1.82 | 1282 | 2.01 | 1364 | 2.21 | 1445 | 2.41 | 1527 | 2.62 | 1608 | 2.85 | 1684 | 3.07
3600 | 3226 | 1162 | 1.91 | 1248 | 2.11 | 1329 | 2.32 | 1407 | 2.52 | 1484 | 2.73 | 1561 | 2.95 | 1638 | 3.18 | 1714 | 3.42 | 1853 | 3.89
3800 | 3405 | 1216 | 2.22 | 1300 | 2.44 | 1377 | 2.65 | 1452 | 2.87 | 1525 | 3.08 | 1597 | 3.3 | 1671 | 3.54 | 1744 | 3.79 | 1883 | 4.29
4000 | 3584 | 1271 | 2.56 | 1352 | 2.8 | 1426 | 3.02 | 1498 | 3.25 | 1568 | 3.47 | 1637 | 3.7 | 1706 | 3.94 | 1776 | 4.2 | 1913 | 4.73
4200 | 3763 | 1326 | 2.94 | 1405 | 3.19 | 1476 | 3.43 | 1545 | 3.66 | 1612 | 3.89 | 1678 | 4.13 | 1744 | 4.38 | 1810 | 4.64
4400 | 3942 | 1381 | 3.35 | 1458 | 3.62 | 1527 | 3.87 | 1593 | 4.11 | 1658 | 4.36 | 1721 | 4.6 | 1784 | 4.86
4600 | 4122 | 1436 | 3.8 | 1511 | 4.09 | 1578 | 4.35 | 1642 | 4.6 | 1704 | 4.86
4800 | 4301 | 1492 | 4.29 | 1564 | 4.59 | 1630 | 4.87
5000 | 4480 | 1548 | 4.82
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 1225DIDWCFAB
1225DIDWCFAB · 12.25" Wheel Diameter · Class R max 2200 RPM Class K max 2500 RPM
Outlet velocity OV (FPM) = 0.71275 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 4" |  | 5" |  | 6" |  | 7"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1100 | 784 | 944 | 0.37 | 1146 | 0.58
1300 | 927 | 942 | 0.43 | 1155 | 0.66 | 1325 | 0.91
1500 | 1069 | 935 | 0.48 | 1156 | 0.74 | 1334 | 1.02 | 1484 | 1.3
2000 | 1426 | 896 | 0.62 | 1135 | 0.95 | 1327 | 1.29 | 1491 | 1.64 | 1635 | 2 | 1882 | 2.75 | 2092 | 3.52
2500 | 1782 | 922 | 0.86 | 1098 | 1.16 | 1287 | 1.54 | 1473 | 1.98 | 1624 | 2.41 | 1886 | 3.29 | 2111 | 4.21 | 2307 | 5.13 | 2483 | 6.09
3000 | 2138 | 964 | 1.2 | 1125 | 1.53 | 1271 | 1.89 | 1419 | 2.29 | 1584 | 2.79 | 1871 | 3.84 | 2104 | 4.88 | 2311 | 5.95 | 2498 | 7.05
3500 | 2495 | 1012 | 1.63 | 1165 | 2.01 | 1301 | 2.4 | 1428 | 2.81 | 1552 | 3.25 | 1824 | 4.33 | 2085 | 5.56 | 2298 | 6.76 | 2491 | 7.99
4000 | 2851 | 1063 | 2.14 | 1211 | 2.6 | 1341 | 3.04 | 1461 | 3.48 | 1574 | 3.94 | 1791 | 4.93 | 2028 | 6.15 | 2270 | 7.56 | 2474 | 8.95
4500 | 3207 | 1117 | 2.75 | 1260 | 3.29 | 1388 | 3.81 | 1502 | 4.3 | 1609 | 4.79 | 1811 | 5.83 | 2003 | 6.95 | 2209 | 8.26 | 2430 | 9.82
5000 | 3564 | 1176 | 3.49 | 1313 | 4.11 | 1436 | 4.69 | 1548 | 5.25 | 1651 | 5.8 | 1844 | 6.91 | 2023 | 8.07 | 2196 | 9.31 | 2376 | 10.7
5500 | 3920 | 1243 | 4.4 | 1367 | 5.04 | 1486 | 5.69 | 1596 | 6.34 | 1698 | 6.96 | 1883 | 8.16 | 2055 | 9.39 | 2217 | 10.67 | 2374 | 12.01
6000 | 4276 | 1315 | 5.48 | 1425 | 6.12 | 1540 | 6.86 | 1646 | 7.56 | 1746 | 8.26 | 1928 | 9.61 | 2092 | 10.9 | 2250 | 12.26 | 2398 | 13.65
6500 | 4633 | 1391 | 6.75 | 1490 | 7.41 | 1595 | 8.16 | 1699 | 8.95 | 1796 | 9.72 | 1975 | 11.22 | 2136 | 12.64 | 2286 | 14.05
7000 | 4989 | 1469 | 8.21 | 1560 | 8.9 | 1655 | 9.67 | 1754 | 10.51 | 1849 | 11.36 | 2023 | 12.99 | 2183 | 14.58
7500 | 5346 | 1548 | 9.87 | 1633 | 10.6 | 1720 | 11.39 | 1810 | 12.23 | 1903 | 13.17 | 2073 | 14.94
8000 | 5702 | 1630 | 11.78 | 1709 | 12.55 | 1789 | 13.34 | 1872 | 14.21
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 1350DIDWCFAB
1350DIDWCFAB · 13.5" Wheel Diameter · Class R max 1900 RPM Class K max 2200 RPM
Outlet velocity OV (FPM) = 0.56913 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 4" |  | 5" |  | 6" |  | 7"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1500 | 854 | 818 | 0.43 | 1007 | 0.67 | 1157 | 0.93 | 1282 | 1.21 | 1393 | 1.51
2000 | 1138 | 808 | 0.56 | 997 | 0.86 | 1160 | 1.17 | 1300 | 1.49 | 1422 | 1.82 | 1629 | 2.53 | 1804 | 3.32 | 1958 | 4.15
2500 | 1423 | 800 | 0.7 | 988 | 1.05 | 1146 | 1.42 | 1289 | 1.8 | 1420 | 2.19 | 1645 | 2.99 | 1834 | 3.83 | 1999 | 4.72 | 2145 | 5.66
3000 | 1707 | 801 | 0.88 | 980 | 1.25 | 1139 | 1.67 | 1279 | 2.11 | 1405 | 2.56 | 1636 | 3.48 | 1838 | 4.42 | 2014 | 5.39 | 2171 | 6.4
3500 | 1992 | 813 | 1.11 | 980 | 1.51 | 1132 | 1.95 | 1270 | 2.43 | 1398 | 2.94 | 1622 | 3.98 | 1825 | 5.05 | 2009 | 6.13 | 2175 | 7.24
4000 | 2277 | 836 | 1.42 | 988 | 1.83 | 1131 | 2.29 | 1265 | 2.8 | 1389 | 3.33 | 1615 | 4.48 | 1812 | 5.68 | 1993 | 6.88 | 2163 | 8.11
4500 | 2561 | 868 | 1.8 | 1005 | 2.23 | 1138 | 2.71 | 1265 | 3.24 | 1385 | 3.79 | 1606 | 5 | 1805 | 6.29 | 1984 | 7.64 | 2148 | 8.99
5000 | 2846 | 906 | 2.26 | 1030 | 2.72 | 1152 | 3.21 | 1272 | 3.76 | 1386 | 4.33 | 1600 | 5.58 | 1796 | 6.94 | 1976 | 8.38 | 2141 | 9.87
5500 | 3130 | 950 | 2.81 | 1062 | 3.3 | 1174 | 3.81 | 1285 | 4.37 | 1393 | 4.96 | 1599 | 6.26 | 1790 | 7.67 | 1967 | 9.16 | 2133 | 10.74
6000 | 3415 | 996 | 3.45 | 1100 | 3.97 | 1203 | 4.52 | 1306 | 5.09 | 1407 | 5.7 | 1603 | 7.03 | 1788 | 8.49 | 1961 | 10.03 | 2123 | 11.65
6500 | 3699 | 1044 | 4.18 | 1142 | 4.76 | 1237 | 5.33 | 1332 | 5.92 | 1427 | 6.56 | 1612 | 7.92 | 1789 | 9.4 | 1958 | 11 | 2118 | 12.68
7000 | 3984 | 1094 | 5.02 | 1188 | 5.66 | 1276 | 6.26 | 1364 | 6.88 | 1453 | 7.54 | 1627 | 8.93 | 1797 | 10.46 | 1959 | 12.08 | 2115 | 13.81
7500 | 4268 | 1147 | 5.99 | 1235 | 6.67 | 1319 | 7.32 | 1401 | 7.97 | 1483 | 8.64 | 1647 | 10.07 | 1809 | 11.64 | 1965 | 13.3
8000 | 4553 | 1201 | 7.08 | 1283 | 7.79 | 1364 | 8.51 | 1441 | 9.19 | 1518 | 9.89 | 1673 | 11.38 | 1825 | 12.95 | 1976 | 14.67
9000 | 5122 | 1317 | 9.74 | 1385 | 10.45 | 1458 | 11.25 | 1530 | 12.06 | 1599 | 12.83 | 1736 | 14.42
10000 | 5691 | 1437 | 13.03 | 1494 | 13.74 | 1558 | 14.59
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 1500DIDWCFAB
1500DIDWCFAB · 15" Wheel Diameter · Class R max 1600 RPM Class K max 2000 RPM
Outlet velocity OV (FPM) = 0.45267 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 4" |  | 5" |  | 6" |  | 7"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2000 | 905 | 720 | 0.58 | 889 | 0.89 | 1023 | 1.23 | 1135 | 1.59 | 1233 | 1.98
2500 | 1132 | 713 | 0.7 | 881 | 1.08 | 1025 | 1.47 | 1147 | 1.87 | 1254 | 2.29 | 1435 | 3.2 | 1587 | 4.19 | 1723 | 5.26
3000 | 1358 | 707 | 0.83 | 874 | 1.27 | 1015 | 1.72 | 1142 | 2.18 | 1256 | 2.65 | 1450 | 3.64 | 1612 | 4.68 | 1754 | 5.81 | 1881 | 7
3500 | 1584 | 705 | 0.99 | 868 | 1.46 | 1009 | 1.97 | 1132 | 2.49 | 1247 | 3.03 | 1450 | 4.12 | 1622 | 5.25 | 1772 | 6.43 | 1906 | 7.69
4000 | 1811 | 709 | 1.19 | 864 | 1.68 | 1003 | 2.22 | 1128 | 2.81 | 1238 | 3.4 | 1440 | 4.61 | 1620 | 5.86 | 1777 | 7.13 | 1918 | 8.46
4500 | 2037 | 718 | 1.44 | 864 | 1.94 | 999 | 2.51 | 1121 | 3.12 | 1234 | 3.78 | 1431 | 5.12 | 1610 | 6.49 | 1772 | 7.88 | 1919 | 9.3
5000 | 2263 | 733 | 1.73 | 869 | 2.25 | 998 | 2.85 | 1117 | 3.49 | 1227 | 4.16 | 1427 | 5.62 | 1600 | 7.11 | 1762 | 8.64 | 1912 | 10.18
5500 | 2490 | 753 | 2.09 | 879 | 2.63 | 1001 | 3.24 | 1115 | 3.89 | 1223 | 4.6 | 1420 | 6.11 | 1596 | 7.74 | 1753 | 9.39 | 1901 | 11.06
6000 | 2716 | 777 | 2.51 | 893 | 3.06 | 1008 | 3.69 | 1117 | 4.36 | 1222 | 5.1 | 1414 | 6.65 | 1590 | 8.36 | 1749 | 10.15 | 1892 | 11.93
6500 | 2942 | 804 | 2.98 | 912 | 3.57 | 1019 | 4.22 | 1123 | 4.91 | 1223 | 5.65 | 1412 | 7.28 | 1583 | 9.01 | 1743 | 10.89 | 1889 | 12.82
7000 | 3169 | 834 | 3.54 | 934 | 4.15 | 1034 | 4.81 | 1132 | 5.52 | 1229 | 6.29 | 1411 | 7.95 | 1580 | 9.75 | 1736 | 11.65 | 1883 | 13.68
8000 | 3621 | 899 | 4.86 | 987 | 5.54 | 1075 | 6.26 | 1162 | 7 | 1249 | 7.81 | 1418 | 9.54 | 1577 | 11.41 | 1729 | 13.44 | 1871 | 15.55
9000 | 4074 | 966 | 6.47 | 1049 | 7.29 | 1127 | 8.07 | 1204 | 8.86 | 1282 | 9.69 | 1436 | 11.49 | 1586 | 13.46 | 1729 | 15.54 | 1866 | 17.75
10000 | 4527 | 1039 | 8.47 | 1114 | 9.37 | 1186 | 10.25 | 1256 | 11.11 | 1326 | 12 | 1466 | 13.87 | 1604 | 15.9 | 1739 | 18.06
11000 | 4979 | 1117 | 10.92 | 1182 | 11.84 | 1250 | 12.83 | 1315 | 13.79 | 1378 | 14.72 | 1506 | 16.73 | 1633 | 18.81
12000 | 5432 | 1198 | 13.86 | 1254 | 14.76 | 1316 | 15.82 | 1378 | 16.91 | 1437 | 17.94
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 1650DIDWCFAB
1650DIDWCFAB · 16.5" Wheel Diameter · Class R max 1400 RPM Class K max 1800 RPM
Outlet velocity OV (FPM) = 0.36143 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 4" |  | 5" |  | 6" |  | 7"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2000 | 723 | 644 | 0.6 | 782 | 0.95 | 891 | 1.34
2500 | 904 | 640 | 0.72 | 789 | 1.12 | 908 | 1.55 | 1007 | 2 | 1094 | 2.5
3000 | 1084 | 635 | 0.85 | 785 | 1.3 | 911 | 1.78 | 1018 | 2.27 | 1110 | 2.79 | 1268 | 3.93 | 1402 | 5.17
3500 | 1265 | 631 | 0.98 | 778 | 1.49 | 906 | 2.03 | 1018 | 2.58 | 1116 | 3.14 | 1283 | 4.34 | 1423 | 5.63 | 1545 | 7.01 | 1656 | 8.49
4000 | 1446 | 627 | 1.11 | 775 | 1.68 | 899 | 2.28 | 1011 | 2.88 | 1113 | 3.5 | 1289 | 4.8 | 1436 | 6.15 | 1564 | 7.6 | 1678 | 9.12
4500 | 1626 | 626 | 1.28 | 770 | 1.87 | 896 | 2.53 | 1005 | 3.2 | 1106 | 3.88 | 1287 | 5.28 | 1441 | 6.73 | 1575 | 8.25 | 1694 | 9.83
5000 | 1807 | 629 | 1.48 | 768 | 2.1 | 891 | 2.78 | 1002 | 3.52 | 1100 | 4.26 | 1280 | 5.78 | 1439 | 7.34 | 1578 | 8.94 | 1703 | 10.62
6000 | 2169 | 643 | 1.99 | 769 | 2.64 | 886 | 3.37 | 993 | 4.16 | 1093 | 5.01 | 1269 | 6.79 | 1425 | 8.59 | 1570 | 10.44 | 1702 | 12.31
7000 | 2530 | 669 | 2.67 | 781 | 3.36 | 889 | 4.13 | 990 | 4.96 | 1086 | 5.86 | 1261 | 7.78 | 1417 | 9.84 | 1556 | 11.94 | 1688 | 14.07
8000 | 2891 | 705 | 3.55 | 803 | 4.27 | 900 | 5.07 | 995 | 5.95 | 1085 | 6.88 | 1254 | 8.91 | 1408 | 11.1 | 1550 | 13.44 | 1679 | 15.84
9000 | 3253 | 746 | 4.63 | 834 | 5.43 | 921 | 6.26 | 1008 | 7.18 | 1092 | 8.14 | 1253 | 10.26 | 1402 | 12.54 | 1541 | 14.99 | 1671 | 17.57
10000 | 3614 | 791 | 5.94 | 871 | 6.81 | 950 | 7.71 | 1029 | 8.66 | 1106 | 9.65 | 1258 | 11.85 | 1401 | 14.22 | 1536 | 16.77 | 1662 | 19.42
11000 | 3976 | 838 | 7.49 | 913 | 8.47 | 985 | 9.44 | 1056 | 10.41 | 1128 | 11.46 | 1269 | 13.72 | 1405 | 16.17 | 1534 | 18.77
12000 | 4337 | 887 | 9.3 | 958 | 10.41 | 1024 | 11.43 | 1090 | 12.5 | 1156 | 13.6 | 1286 | 15.89 | 1414 | 18.4
13000 | 4699 | 940 | 11.48 | 1004 | 12.61 | 1067 | 13.76 | 1128 | 14.89 | 1189 | 16.05 | 1310 | 18.44
14000 | 5060 | 995 | 14 | 1052 | 15.14 | 1113 | 16.44 | 1170 | 17.64 | 1226 | 18.84
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 1825DIDWCFAB
1825DIDWCFAB · 18.25" Wheel Diameter · Class R max 1300 RPM Class K max 1600 RPM
Outlet velocity OV (FPM) = 0.28693 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 4" |  | 5" |  | 6" |  | 7"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2000 | 574 | 589 | 0.68 | 707 | 1.09
3000 | 861 | 585 | 0.87 | 726 | 1.43 | 836 | 2 | 926 | 2.59 | 1006 | 3.22 | 1145 | 4.53
4000 | 1148 | 565 | 1.05 | 708 | 1.68 | 832 | 2.39 | 937 | 3.13 | 1027 | 3.89 | 1177 | 5.44 | 1303 | 7.07 | 1414 | 8.76 | 1515 | 10.52
5000 | 1435 | 556 | 1.29 | 691 | 1.96 | 809 | 2.72 | 918 | 3.55 | 1018 | 4.45 | 1186 | 6.3 | 1325 | 8.2 | 1444 | 10.15 | 1550 | 12.15
6000 | 1722 | 567 | 1.67 | 681 | 2.32 | 794 | 3.11 | 898 | 3.99 | 993 | 4.93 | 1170 | 7 | 1322 | 9.19 | 1453 | 11.43 | 1568 | 13.7
7000 | 2009 | 585 | 2.16 | 690 | 2.85 | 787 | 3.62 | 884 | 4.51 | 978 | 5.51 | 1145 | 7.63 | 1300 | 9.99 | 1440 | 12.5 | 1565 | 15.08
8000 | 2295 | 607 | 2.77 | 705 | 3.51 | 795 | 4.32 | 880 | 5.19 | 965 | 6.17 | 1131 | 8.42 | 1277 | 10.83 | 1416 | 13.47 | 1546 | 16.27
9000 | 2582 | 631 | 3.49 | 725 | 4.32 | 810 | 5.18 | 890 | 6.1 | 966 | 7.07 | 1116 | 9.26 | 1263 | 11.81 | 1395 | 14.5 | 1521 | 17.39
10000 | 2869 | 659 | 4.37 | 748 | 5.29 | 829 | 6.21 | 905 | 7.18 | 977 | 8.19 | 1113 | 10.36 | 1249 | 12.88 | 1382 | 15.72 | 1504 | 18.68
11000 | 3156 | 689 | 5.42 | 773 | 6.4 | 850 | 7.39 | 923 | 8.43 | 992 | 9.49 | 1121 | 11.74 | 1244 | 14.21 | 1367 | 16.97
12000 | 3443 | 720 | 6.63 | 800 | 7.68 | 874 | 8.76 | 944 | 9.87 | 1010 | 10.99 | 1134 | 13.34 | 1250 | 15.86 | 1362 | 18.56
13000 | 3730 | 754 | 8.06 | 829 | 9.16 | 900 | 10.32 | 967 | 11.5 | 1031 | 12.71 | 1150 | 15.16 | 1262 | 17.77
14000 | 4017 | 789 | 9.66 | 860 | 10.88 | 928 | 12.09 | 992 | 13.34 | 1054 | 14.64 | 1169 | 17.23 | 1277 | 19.94
15000 | 4304 | 825 | 11.45 | 892 | 12.8 | 957 | 14.08 | 1019 | 15.41 | 1078 | 16.76 | 1190 | 19.53
16000 | 4591 | 862 | 13.46 | 926 | 14.97 | 988 | 16.36 | 1047 | 17.71 | 1105 | 19.18
17000 | 4878 | 900 | 15.72 | 961 | 17.37 | 1019 | 18.82
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 2000DIDWCFAB
2000DIDWCFAB · 20" Wheel Diameter · Class R max 1100 RPM Class K max 1300 RPM
Outlet velocity OV (FPM) = 0.22825 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3000 | 685 | 534 | 0.95 | 649 | 1.54 | 739 | 2.15 | 817 | 2.8
4000 | 913 | 521 | 1.13 | 652 | 1.84 | 755 | 2.6 | 840 | 3.38 | 913 | 4.18 | 978 | 4.99 | 1039 | 5.86
5000 | 1141 | 508 | 1.31 | 636 | 2.09 | 749 | 2.98 | 844 | 3.9 | 925 | 4.84 | 997 | 5.81 | 1061 | 6.78 | 1175 | 8.8 | 1275 | 10.9
6000 | 1370 | 501 | 1.55 | 624 | 2.37 | 731 | 3.3 | 830 | 4.32 | 919 | 5.41 | 997 | 6.5 | 1068 | 7.63 | 1191 | 9.92 | 1297 | 12.27
7000 | 1598 | 507 | 1.9 | 614 | 2.7 | 720 | 3.69 | 813 | 4.74 | 901 | 5.88 | 984 | 7.11 | 1060 | 8.37 | 1193 | 10.95
8000 | 1826 | 518 | 2.34 | 616 | 3.16 | 710 | 4.12 | 803 | 5.24 | 887 | 6.42 | 966 | 7.67 | 1042 | 9 | 1182 | 11.83
9000 | 2054 | 532 | 2.87 | 625 | 3.74 | 710 | 4.71 | 793 | 5.78 | 877 | 7.03 | 955 | 8.34 | 1026 | 9.68 | 1164 | 12.63 | 1291 | 15.79
10000 | 2282 | 548 | 3.49 | 637 | 4.44 | 717 | 5.43 | 793 | 6.51 | 868 | 7.71 | 944 | 9.06 | 1017 | 10.5 | 1148 | 13.47 | 1272 | 16.72
11000 | 2511 | 567 | 4.24 | 651 | 5.24 | 728 | 6.29 | 800 | 7.41 | 869 | 8.61 | 937 | 9.9 | 1006 | 11.34 | 1139 | 14.49 | 1257 | 17.76
12000 | 2739 | 586 | 5.07 | 667 | 6.16 | 741 | 7.28 | 811 | 8.47 | 876 | 9.68 | 939 | 10.98 | 1001 | 12.35 | 1128 | 15.53 | 1248 | 18.98
13000 | 2967 | 607 | 6.04 | 685 | 7.22 | 756 | 8.41 | 823 | 9.65 | 887 | 10.95 | 947 | 12.27 | 1005 | 13.65 | 1120 | 16.69
14000 | 3196 | 630 | 7.18 | 704 | 8.41 | 773 | 9.69 | 837 | 10.97 | 898 | 12.31 | 957 | 13.71 | 1013 | 15.14 | 1121 | 18.19
15000 | 3424 | 653 | 8.44 | 724 | 9.73 | 791 | 11.11 | 853 | 12.47 | 912 | 13.87 | 969 | 15.33 | 1024 | 16.83 | 1127 | 19.92
16000 | 3652 | 678 | 9.89 | 746 | 11.26 | 810 | 12.68 | 870 | 14.12 | 928 | 15.63 | 982 | 17.09 | 1035 | 18.64
18000 | 4108 | 729 | 13.17 | 791 | 14.78 | 851 | 16.34 | 907 | 17.91 | 962 | 19.6
20000 | 4565 | 784 | 17.22 | 840 | 19.05
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 2225DIDWCFAB
2225DIDWCFAB · 22.25" Wheel Diameter · Class R max 900 RPM Class K max 1200 RPM
Outlet velocity OV (FPM) = 0.1817 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
4000 | 727 | 476 | 1.24 | 582 | 2.01 | 664 | 2.8 | 734 | 3.64 | 797 | 4.54
5000 | 908 | 466 | 1.41 | 583 | 2.31 | 674 | 3.25 | 750 | 4.23 | 815 | 5.22 | 874 | 6.26 | 928 | 7.33
6000 | 1090 | 456 | 1.59 | 572 | 2.56 | 671 | 3.63 | 754 | 4.75 | 825 | 5.89 | 888 | 7.06 | 944 | 8.24 | 1045 | 10.72 | 1134 | 13.3
7000 | 1272 | 449 | 1.8 | 561 | 2.82 | 659 | 3.95 | 748 | 5.22 | 825 | 6.5 | 893 | 7.82 | 953 | 9.13 | 1060 | 11.88 | 1151 | 14.66
8000 | 1454 | 448 | 2.09 | 553 | 3.11 | 648 | 4.3 | 735 | 5.61 | 815 | 7 | 887 | 8.45 | 953 | 9.95 | 1066 | 12.95 | 1164 | 16.05
9000 | 1635 | 454 | 2.46 | 548 | 3.47 | 641 | 4.7 | 724 | 6.04 | 802 | 7.48 | 876 | 9.04 | 944 | 10.63 | 1065 | 13.95 | 1169 | 17.35
10000 | 1817 | 462 | 2.91 | 550 | 3.95 | 634 | 5.14 | 717 | 6.54 | 792 | 8.01 | 863 | 9.59 | 931 | 11.26 | 1056 | 14.8 | 1166 | 18.5
11000 | 1999 | 472 | 3.43 | 556 | 4.51 | 633 | 5.7 | 710 | 7.08 | 785 | 8.62 | 855 | 10.26 | 919 | 11.93 | 1043 | 15.59 | 1157 | 19.54
12000 | 2180 | 483 | 4.02 | 564 | 5.17 | 637 | 6.39 | 707 | 7.73 | 778 | 9.28 | 847 | 10.95 | 912 | 12.71 | 1031 | 16.43 | 1144 | 20.48
13000 | 2362 | 496 | 4.71 | 573 | 5.91 | 644 | 7.19 | 710 | 8.55 | 775 | 10.06 | 840 | 11.72 | 904 | 13.51 | 1022 | 17.33 | 1131 | 21.44
14000 | 2544 | 509 | 5.47 | 584 | 6.76 | 652 | 8.08 | 716 | 9.49 | 777 | 11 | 837 | 12.63 | 897 | 14.39 | 1015 | 18.34 | 1121 | 22.49
16000 | 2907 | 538 | 7.28 | 608 | 8.73 | 672 | 10.19 | 732 | 11.71 | 790 | 13.34 | 844 | 14.98 | 897 | 16.74 | 1002 | 20.58 | 1107 | 24.95
18000 | 3271 | 570 | 9.55 | 635 | 11.1 | 696 | 12.76 | 753 | 14.43 | 807 | 16.14 | 859 | 17.92 | 908 | 19.7 | 1003 | 23.56
20000 | 3634 | 604 | 12.27 | 665 | 13.99 | 723 | 15.82 | 777 | 17.64 | 828 | 19.47 | 877 | 21.35 | 924 | 23.25
22000 | 3997 | 641 | 15.53 | 697 | 17.43 | 751 | 19.32 | 803 | 21.35 | 852 | 23.36
24000 | 4361 | 679 | 19.28 | 731 | 21.45 | 782 | 23.51
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 2450DIDWCFAB
2450DIDWCFAB · 24.5" Wheel Diameter · Class R max 800 RPM Class K max 1000 RPM
Outlet velocity OV (FPM) = 0.1448 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
4000 | 579 | 422 | 1.35 | 507 | 2.17
5000 | 724 | 424 | 1.56 | 517 | 2.52 | 590 | 3.52 | 652 | 4.57
6000 | 869 | 417 | 1.73 | 519 | 2.83 | 598 | 3.97 | 664 | 5.16 | 721 | 6.38 | 773 | 7.66 | 820 | 8.96
7000 | 1014 | 408 | 1.89 | 514 | 3.1 | 600 | 4.4 | 670 | 5.71 | 731 | 7.08 | 785 | 8.48 | 833 | 9.87 | 921 | 12.85
8000 | 1158 | 403 | 2.09 | 505 | 3.34 | 594 | 4.74 | 670 | 6.22 | 735 | 7.73 | 792 | 9.25 | 843 | 10.8 | 934 | 14.03
9000 | 1303 | 398 | 2.3 | 498 | 3.6 | 585 | 5.06 | 664 | 6.66 | 733 | 8.31 | 794 | 10 | 848 | 11.68 | 943 | 15.16
10000 | 1448 | 398 | 2.6 | 493 | 3.91 | 577 | 5.4 | 655 | 7.06 | 726 | 8.81 | 790 | 10.63 | 848 | 12.5 | 948 | 16.27
12000 | 1738 | 407 | 3.38 | 487 | 4.65 | 567 | 6.22 | 641 | 7.94 | 708 | 9.77 | 773 | 11.76 | 834 | 13.84 | 944 | 18.2
14000 | 2027 | 420 | 4.37 | 495 | 5.77 | 563 | 7.27 | 631 | 9.01 | 698 | 10.98 | 760 | 13.05 | 817 | 15.17 | 927 | 19.8
16000 | 2317 | 437 | 5.65 | 507 | 7.15 | 571 | 8.76 | 630 | 10.43 | 689 | 12.33 | 749 | 14.47 | 807 | 16.77 | 911 | 21.5
18000 | 2606 | 455 | 7.13 | 522 | 8.83 | 582 | 10.52 | 638 | 12.3 | 692 | 14.23 | 744 | 16.25 | 797 | 18.51 | 901 | 23.5
20000 | 2896 | 476 | 8.98 | 539 | 10.81 | 596 | 12.63 | 650 | 14.56 | 701 | 16.56 | 749 | 18.6 | 797 | 20.85
22000 | 3186 | 498 | 11.15 | 557 | 13.06 | 612 | 15.08 | 664 | 17.17 | 712 | 19.22 | 759 | 21.43 | 804 | 23.72
24000 | 3475 | 522 | 13.73 | 578 | 15.79 | 630 | 17.92 | 680 | 20.18 | 726 | 22.35 | 771 | 24.67
26000 | 3765 | 546 | 16.59 | 599 | 18.83 | 650 | 21.21 | 697 | 23.53
28000 | 4054 | 572 | 19.92 | 622 | 22.4 | 670 | 24.82
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 2700DIDWCFAB
2700DIDWCFAB · 27" Wheel Diameter · Class R max 700 RPM Class K max 900 RPM
Outlet velocity OV (FPM) = 0.11521 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
4000 | 461 | 373 | 1.45
5000 | 576 | 379 | 1.68 | 457 | 2.68 | 520 | 3.83
6000 | 691 | 380 | 1.92 | 464 | 3.04 | 530 | 4.24 | 586 | 5.55
7000 | 806 | 378 | 2.14 | 465 | 3.39 | 535 | 4.69 | 595 | 6.1 | 646 | 7.56 | 692 | 9.11
8000 | 922 | 370 | 2.3 | 464 | 3.74 | 537 | 5.18 | 599 | 6.67 | 653 | 8.22 | 702 | 9.89 | 746 | 11.61 | 823 | 15.2
10000 | 1152 | 365 | 2.81 | 452 | 4.29 | 534 | 6.09 | 600 | 7.88 | 658 | 9.68 | 710 | 11.5 | 758 | 13.42 | 842 | 17.37
12000 | 1383 | 367 | 3.48 | 446 | 5.02 | 519 | 6.78 | 591 | 8.85 | 655 | 11.04 | 709 | 13.15 | 759 | 15.3 | 849 | 19.72
14000 | 1613 | 368 | 4.18 | 449 | 6.04 | 515 | 7.81 | 577 | 9.76 | 640 | 12.04 | 701 | 14.55 | 755 | 17.06 | 848 | 22.06
16000 | 1843 | 375 | 5.16 | 450 | 7.07 | 518 | 9.17 | 577 | 11.25 | 631 | 13.36 | 686 | 15.79 | 741 | 18.47 | 843 | 24.23
18000 | 2074 | 384 | 6.34 | 454 | 8.31 | 519 | 10.52 | 579 | 12.9 | 632 | 15.2 | 682 | 17.61 | 730 | 20.12 | 827 | 25.85
20000 | 2304 | 395 | 7.77 | 461 | 9.81 | 522 | 12.08 | 580 | 14.58 | 635 | 17.28 | 684 | 19.86 | 729 | 22.4 | 816 | 27.91
22000 | 2535 | 408 | 9.39 | 470 | 11.6 | 528 | 13.95 | 582 | 16.44 | 635 | 19.23 | 686 | 22.23 | 732 | 25.1
24000 | 2765 | 423 | 11.25 | 480 | 13.65 | 536 | 16.11 | 588 | 18.73 | 638 | 21.55 | 686 | 24.52 | 733 | 27.74
26000 | 2995 | 442 | 13.57 | 493 | 16.03 | 546 | 18.69 | 596 | 21.37 | 643 | 24.19 | 689 | 27.23
28000 | 3226 | 464 | 16.38 | 507 | 18.62 | 556 | 21.45 | 605 | 24.33 | 651 | 27.31
32000 | 3687 | 511 | 23.3 | 542 | 25.09 | 583 | 28.07
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 3000DIDWCFAB
3000DIDWCFAB · 30" Wheel Diameter · Class K max 800 RPM
Outlet velocity OV (FPM) = 0.09162 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
6000 | 550 | 321 | 1.88 | 386 | 2.98
7000 | 641 | 323 | 2.1 | 391 | 3.32 | 447 | 4.65
8000 | 733 | 323 | 2.3 | 394 | 3.65 | 451 | 5.07 | 500 | 6.56 | 544 | 8.15
9000 | 825 | 322 | 2.51 | 396 | 3.99 | 455 | 5.53 | 505 | 7.13 | 549 | 8.79 | 589 | 10.51 | 626 | 12.29
10000 | 916 | 320 | 2.71 | 396 | 4.31 | 457 | 5.98 | 508 | 7.67 | 554 | 9.48 | 595 | 11.33 | 632 | 13.19 | 700 | 17.14
11000 | 1008 | 319 | 2.94 | 394 | 4.59 | 457 | 6.38 | 510 | 8.22 | 557 | 10.14 | 599 | 12.1 | 637 | 14.08 | 706 | 18.26 | 767 | 22.59
12000 | 1099 | 319 | 3.21 | 393 | 4.92 | 456 | 6.78 | 511 | 8.77 | 559 | 10.79 | 602 | 12.87 | 641 | 14.98 | 711 | 19.36 | 773 | 23.92
14000 | 1283 | 317 | 3.77 | 391 | 5.62 | 453 | 7.61 | 509 | 9.77 | 560 | 12.09 | 605 | 14.41 | 646 | 16.77 | 719 | 21.63 | 783 | 26.64
16000 | 1466 | 318 | 4.34 | 389 | 6.43 | 452 | 8.58 | 506 | 10.83 | 557 | 13.29 | 604 | 15.87 | 646 | 18.41 | 722 | 23.75 | 789 | 29.28
18000 | 1649 | 322 | 5.03 | 388 | 7.27 | 449 | 9.59 | 505 | 12.05 | 554 | 14.57 | 601 | 17.31 | 644 | 20.07 | 722 | 25.83
20000 | 1832 | 329 | 5.95 | 390 | 8.17 | 448 | 10.75 | 503 | 13.38 | 553 | 16.05 | 598 | 18.82 | 641 | 21.77 | 720 | 27.9
22000 | 2016 | 337 | 7.01 | 395 | 9.26 | 449 | 11.91 | 501 | 14.77 | 550 | 17.58 | 597 | 20.6 | 639 | 23.6
26000 | 2382 | 356 | 9.7 | 408 | 12.02 | 457 | 14.67 | 504 | 17.73 | 549 | 21.04 | 592 | 24.33 | 635 | 27.8
30000 | 2749 | 378 | 13.15 | 426 | 15.7 | 471 | 18.48 | 514 | 21.53 | 555 | 24.84 | 595 | 28.52
34000 | 3115 | 401 | 17.16 | 447 | 20.38 | 489 | 23.33 | 529 | 26.53 | 567 | 29.88
38000 | 3482 | 425 | 21.84 | 470 | 25.93 | 510 | 29.4
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 3300DIDWCFAB
3300DIDWCFAB · 33" Wheel Diameter · Class K max 700 RPM
Outlet velocity OV (FPM) = 0.07276 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
8000 | 582 | 286 | 2.46 | 345 | 3.91 | 394 | 5.5
10000 | 728 | 287 | 2.88 | 351 | 4.61 | 401 | 6.37 | 444 | 8.23 | 483 | 10.21
12000 | 873 | 286 | 3.31 | 352 | 5.23 | 405 | 7.24 | 451 | 9.39 | 490 | 11.51 | 526 | 13.76 | 560 | 16.16
14000 | 1019 | 284 | 3.75 | 351 | 5.87 | 406 | 8.09 | 454 | 10.47 | 495 | 12.85 | 533 | 15.38 | 567 | 17.92 | 628 | 23.18 | 682 | 28.64
16000 | 1164 | 283 | 4.29 | 348 | 6.46 | 405 | 8.94 | 454 | 11.5 | 498 | 14.22 | 536 | 16.87 | 572 | 19.71 | 635 | 25.44 | 690 | 31.31
18000 | 1310 | 282 | 4.86 | 347 | 7.18 | 403 | 9.79 | 453 | 12.57 | 497 | 15.4 | 538 | 18.44 | 574 | 21.39 | 640 | 27.7 | 697 | 34.09
20000 | 1455 | 283 | 5.45 | 346 | 8.03 | 402 | 10.74 | 450 | 13.55 | 496 | 16.71 | 537 | 19.87 | 575 | 23.16 | 642 | 29.81
22000 | 1601 | 285 | 6.07 | 345 | 8.88 | 400 | 11.72 | 449 | 14.73 | 493 | 17.89 | 535 | 21.31 | 573 | 24.72 | 643 | 32
24000 | 1746 | 289 | 6.89 | 346 | 9.77 | 399 | 12.88 | 448 | 16.02 | 492 | 19.31 | 533 | 22.82 | 571 | 26.38 | 642 | 34.07
26000 | 1892 | 294 | 7.84 | 348 | 10.7 | 398 | 13.97 | 446 | 17.33 | 491 | 20.83 | 531 | 24.34 | 569 | 28.11 | 640 | 36.12
28000 | 2037 | 300 | 8.96 | 351 | 11.77 | 399 | 15.13 | 445 | 18.75 | 489 | 22.39 | 530 | 26.11 | 568 | 30 | 637 | 38.08
30000 | 2183 | 306 | 10.15 | 355 | 13.02 | 402 | 16.49 | 446 | 20.29 | 488 | 24.12 | 529 | 28.08 | 567 | 32.04
35000 | 2547 | 324 | 13.93 | 369 | 17 | 411 | 20.41 | 451 | 24.21 | 490 | 28.56 | 527 | 33.01 | 563 | 37.47
40000 | 2910 | 344 | 18.55 | 386 | 22.1 | 425 | 25.71 | 462 | 29.63 | 497 | 33.72 | 532 | 38.49
45000 | 3274 | 365 | 23.97 | 406 | 28.57 | 442 | 32.37 | 476 | 36.34
50000 | 3638 | 387 | 30.3 | 426 | 35.74
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.

## 3650DIDWCFAB
3650DIDWCFAB · 36.5" Wheel Diameter · Class K max 600 RPM
Outlet velocity OV (FPM) = 0.05787 × CFM (regenerated). Performance: Type B, free inlet / ducted outlet; BHP excludes drive losses.
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1" |  | 1.5" |  | 2" |  | 2.5" |  | 3" |  | 3.5" |  | 4" |  | 5" |  | 6"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
10000 | 579 | 182 | 1.39 | 258 | 3.08 | 311 | 4.88 | 355 | 6.84
12500 | 723 | 181 | 1.68 | 259 | 3.62 | 316 | 5.73 | 361 | 7.91 | 400 | 10.23 | 435 | 12.68
15000 | 868 | 179 | 2 | 257 | 4.12 | 317 | 6.53 | 365 | 9.04 | 406 | 11.67 | 442 | 14.38 | 504 | 20.03
17500 | 1013 | 180 | 2.38 | 256 | 4.7 | 315 | 7.26 | 366 | 10.12 | 409 | 13.06 | 446 | 16.01 | 511 | 22.33 | 566 | 28.87
20000 | 1157 | 183 | 2.83 | 254 | 5.32 | 314 | 8.13 | 364 | 11.1 | 409 | 14.37 | 448 | 17.66 | 515 | 24.51 | 572 | 31.65
22500 | 1302 | 187 | 3.39 | 253 | 6.02 | 313 | 9.04 | 362 | 12.15 | 407 | 15.6 | 448 | 19.28 | 517 | 26.67 | 576 | 34.42
25000 | 1447 | 192 | 4.06 | 255 | 6.83 | 311 | 10.01 | 361 | 13.33 | 405 | 16.91 | 446 | 20.78 | 517 | 28.75 | 578 | 37.12
27500 | 1591 | 198 | 4.88 | 257 | 7.63 | 310 | 11.04 | 360 | 14.67 | 404 | 18.38 | 444 | 22.37 | 516 | 30.86 | 578 | 39.69
30000 | 1736 | 205 | 5.87 | 261 | 8.69 | 311 | 12.15 | 359 | 16.1 | 403 | 20.01 | 443 | 24.14 | 514 | 32.93 | 577 | 42.28
35000 | 2025 | 219 | 8.11 | 271 | 11.31 | 317 | 14.84 | 360 | 19.03 | 401 | 23.54 | 440 | 28.01 | 511 | 37.42 | 573 | 47.45
40000 | 2315 | 235 | 10.94 | 283 | 14.63 | 326 | 18.41 | 365 | 22.43 | 403 | 27.24 | 439 | 32.29 | 509 | 42.85
45000 | 2604 | 251 | 14.2 | 297 | 18.8 | 337 | 22.78 | 374 | 27.09 | 409 | 31.75 | 443 | 37.07 | 507 | 48.42
50000 | 2894 | 269 | 18.24 | 312 | 23.63 | 350 | 28.21 | 384 | 32.48 | 417 | 37.33 | 449 | 42.59
55000 | 3183 | 287 | 22.85 | 327 | 28.98 | 364 | 34.55 | 396 | 39.02 | 428 | 44.28 | 457 | 49.33
60000 | 3472 | 307 | 28.7 | 343 | 35.17 | 378 | 41.41 | 410 | 46.98
65000 | 3762 | 326 | 35.16 | 360 | 42.3 | 393 | 49.18
Blank cells = not rated at that SP/CFM. Ratings exclude appurtenances in the airstream. Class R and Class K share this curve; observe the class max RPM above.