## Index
Forward Curve Single Inlet — Series FC
Belt-Driven Centrifugal Blower — Performance Rating Tables
Ratings basis: AMCA Pub. 211, Installation Type B (Free Inlet, Ducted Outlet)
Model | Wheel Diameter | Tip Speed (FPM) | Capacity Range (CFM)
FC-109 | 9 1/8 in. | 2.39 × RPM | 300 – 1,400
FC-111 | 10 5/8 in. | 2.78 × RPM | 600 – 2,000
FC-112 | 12 5/8 in. | 3.31 × RPM | 800 – 2,600
FC-115 | 15 in. | 3.93 × RPM | 1,200 – 4,000
FC-118 | 18 1/2 in. | 4.75 × RPM | 1,600 – 5,200
FC-120 | 20 in. | 5.24 × RPM | 2,500 – 9,000
FC-122 | 22 in. | 5.76 × RPM | 3,000 – 11,500
FC-126 | 26 in. | 6.80 × RPM | 3,000 – 16,000
FC-130 | 30 1/4 in. | 7.92 × RPM | 6,000 – 22,000
Each model is on its own tab. Volume (CFM) runs down the first column; static pressure (in. WG) runs across the top, each SP split into RPM and BHP. BHP excludes drive losses; ratings exclude airstream appurtenances. See the 'Source Notes' tab for flagged values.

## FC-109
FC-109 · 9 1/8 in. Wheel Diameter · Tip Speed (FPM) = 2.39 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
300 | 670 | 458 | 0.01 | 577 | 0.02 | 706 | 0.03
400 | 893 | 525 | 0.02 | 633 | 0.04 | 723 | 0.05 | 808 | 0.06 | 903 | 0.07
500 | 1116 | 598 | 0.04 | 699 | 0.06 | 782 | 0.07 | 855 | 0.08 | 924 | 0.09 | 992 | 0.11 | 1145 | 0.14
600 | 1339 | 690 | 0.07 | 762 | 0.08 | 847 | 0.1 | 917 | 0.11 | 980 | 0.13 | 1040 | 0.14 | 1154 | 0.17 | 1272 | 0.21
700 | 1563 | 786 | 0.1 | 840 | 0.11 | 913 | 0.13 | 983 | 0.15 | 1044 | 0.17 | 1101 | 0.19 | 1205 | 0.22 | 1304 | 0.26 | 1401 | 0.3 | 1505 | 0.34
800 | 1786 | 886 | 0.15 | 930 | 0.16 | 982 | 0.18 | 1049 | 0.2 | 1111 | 0.22 | 1165 | 0.25 | 1266 | 0.29 | 1357 | 0.33 | 1445 | 0.36 | 1529 | 0.4 | 1616 | 0.45
900 | 2009 | 987 | 0.21 | 1025 | 0.22 | 1066 | 0.24 | 1115 | 0.26 | 1176 | 0.28 | 1234 | 0.31 | 1330 | 0.36 | 1419 | 0.41 | 1501 | 0.45 | 1581 | 0.49 | 1656 | 0.54
1000 | 2232 | 1090 | 0.29 | 1122 | 0.3 | 1158 | 0.31 | 1197 | 0.33 | 1242 | 0.35 | 1296 | 0.38 | 1397 | 0.44 | 1483 | 0.5 | 1563 | 0.56 | 1638 | 0.6 | 1710 | 0.65
1100 | 2455 | 1193 | 0.38 | 1222 | 0.39 | 1253 | 0.41 | 1286 | 0.43 | 1323 | 0.45 | 1364 | 0.47 | 1467 | 0.54 | 1550 | 0.6 | 1627 | 0.66 | 1701 | 0.73 | 1770 | 0.78
1200 | 2679 | 1296 | 0.49 | 1322 | 0.51 | 1350 | 0.52 | 1379 | 0.54 | 1411 | 0.56 | 1445 | 0.58 | 1525 | 0.64 | 1619 | 0.71 | 1694 | 0.78 | 1765 | 0.85 | 1834 | 0.92
1300 | 2902 | 1400 | 0.62 | 1424 | 0.64 | 1449 | 0.65 | 1475 | 0.67 | 1503 | 0.69 | 1532 | 0.71 | 1598 | 0.76 | 1678 | 0.83 | 1764 | 0.92
1400 | 3125 | 1504 | 0.77 | 1526 | 0.79 | 1549 | 0.81 | 1573 | 0.83 | 1598 | 0.85 | 1624 | 0.87
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-111
FC-111 · 10 5/8 in. Wheel Diameter · Tip Speed (FPM) = 2.78 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
600 | 910 | 445 | 0.04 | 545 | 0.06 | 635 | 0.08 | 710 | 0.1 | 785 | 0.11 | 857 | 0.13
700 | 1062 | 480 | 0.06 | 580 | 0.08 | 661 | 0.1 | 734 | 0.12 | 799 | 0.14 | 864 | 0.16 | 990 | 0.21
800 | 1214 | 521 | 0.09 | 617 | 0.11 | 690 | 0.13 | 760 | 0.15 | 825 | 0.18 | 882 | 0.2 | 998 | 0.25 | 1107 | 0.29
900 | 1366 | 576 | 0.12 | 645 | 0.14 | 723 | 0.16 | 790 | 0.19 | 854 | 0.22 | 910 | 0.24 | 1017 | 0.3 | 1117 | 0.35 | 1218 | 0.4
1000 | 1517 | 628 | 0.16 | 682 | 0.18 | 758 | 0.2 | 823 | 0.23 | 881 | 0.26 | 939 | 0.29 | 1040 | 0.35 | 1136 | 0.41 | 1223 | 0.47 | 1313 | 0.52 | 1400 | 0.59
1100 | 1669 | 682 | 0.21 | 722 | 0.23 | 791 | 0.25 | 858 | 0.28 | 917 | 0.32 | 968 | 0.35 | 1064 | 0.41 | 1159 | 0.48 | 1241 | 0.54 | 1322 | 0.6 | 1407 | 0.67
1200 | 1821 | 741 | 0.28 | 755 | 0.29 | 824 | 0.31 | 890 | 0.34 | 945 | 0.38 | 1000 | 0.41 | 1098 | 0.48 | 1183 | 0.55 | 1268 | 0.62 | 1342 | 0.69 | 1420 | 0.76
1300 | 1973 | 800 | 0.36 | 827 | 0.36 | 863 | 0.38 | 922 | 0.41 | 980 | 0.45 | 1037 | 0.48 | 1125 | 0.56 | 1217 | 0.63 | 1297 | 0.71 | 1370 | 0.79 | 1441 | 0.86
1400 | 2124 | 859 | 0.44 | 880 | 0.44 | 915 | 0.46 | 960 | 0.49 | 1017 | 0.52 | 1065 | 0.56 | 1160 | 0.64 | 1242 | 0.73 | 1321 | 0.81 | 1397 | 0.89 | 1465 | 0.98
1500 | 2276 | 917 | 0.54 | 938 | 0.54 | 962 | 0.56 | 1000 | 0.58 | 1050 | 0.61 | 1100 | 0.65 | 1192 | 0.74 | 1276 | 0.83 | 1352 | 0.92 | 1422 | 1 | 1495 | 1.09
1600 | 2428 | 975 | 0.65 | 994 | 0.66 | 1019 | 0.68 | 1044 | 0.69 | 1085 | 0.72 | 1136 | 0.76 | 1225 | 0.85 | 1308 | 0.94 | 1382 | 1.04 | 1456 | 1.13 | 1521 | 1.22
1700 | 2580 | 1035 | 0.78 | 1055 | 0.79 | 1075 | 0.79 | 1098 | 0.82 | 1130 | 0.84 | 1170 | 0.88 | 1260 | 0.96 | 1340 | 1.07 | 1418 | 1.16 | 1483 | 1.26 | 1555 | 1.36
1800 | 2731 | 1092 | 0.92 | 1110 | 0.94 | 1125 | 0.94 | 1150 | 0.97 | 1177 | 0.98 | 1210 | 1.01 | 1295 | 1.1 | 1377 | 1.2 | 1450 | 1.31 | 1518 | 1.41
1900 | 2883 | 1150 | 1.09 | 1170 | 1.1 | 1180 | 1.11 | 1205 | 1.12 | 1225 | 1.15 | 1255 | 1.17 | 1330 | 1.25 | 1408 | 1.35 | 1481 | 1.46
2000 | 3035 | 1210 | 1.27 | 1225 | 1.28 | 1240 | 1.28 | 1259 | 1.29 | 1279 | 1.33 | 1300 | 1.35 | 1365 | 1.41
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-112
FC-112 · 12 5/8 in. Wheel Diameter · Tip Speed (FPM) = 3.31 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
800 | 1054 | 400 | 0.06 | 481 | 0.08 | 551 | 0.11 | 611 | 0.14 | 667 | 0.15 | 721 | 0.18 | 835 | 0.24
1000 | 1318 | 455 | 0.1 | 530 | 0.13 | 594 | 0.16 | 651 | 0.2 | 704 | 0.23 | 752 | 0.25 | 842 | 0.31 | 930 | 0.37 | 1020 | 0.43
1200 | 1581 | 511 | 0.16 | 584 | 0.19 | 642 | 0.23 | 696 | 0.27 | 746 | 0.31 | 793 | 0.35 | 877 | 0.42 | 955 | 0.48 | 1028 | 0.55 | 1101 | 0.62 | 1176 | 0.7
1400 | 1845 | 570 | 0.23 | 639 | 0.27 | 695 | 0.32 | 746 | 0.36 | 792 | 0.41 | 837 | 0.45 | 918 | 0.55 | 992 | 0.62 | 1061 | 0.7 | 1127 | 0.78 | 1190 | 0.86
1600 | 2108 | 630 | 0.33 | 694 | 0.38 | 750 | 0.43 | 799 | 0.48 | 842 | 0.54 | 885 | 0.58 | 962 | 0.68 | 1035 | 0.79 | 1101 | 0.88 | 1163 | 0.97 | 1222 | 1.06
1800 | 2372 | 693 | 0.46 | 753 | 0.51 | 805 | 0.57 | 853 | 0.62 | 896 | 0.7 | 936 | 0.75 | 1010 | 0.86 | 1078 | 0.96 | 1143 | 1.09 | 1204 | 1.2 | 1261 | 1.3
2000 | 2635 | 758 | 0.62 | 812 | 0.68 | 862 | 0.73 | 909 | 0.79 | 951 | 0.89 | 989 | 0.94 | 1060 | 1.06 | 1126 | 1.18 | 1187 | 1.3 | 1248 | 1.43 | 1303 | 1.56
2200 | 2899 | 824 | 0.81 | 872 | 0.87 | 920 | 0.93 | 965 | 1 | 1006 | 1.09 | 1045 | 1.18 | 1112 | 1.29 | 1176 | 1.43 | 1235 | 1.56 | 1292 | 1.69 | 1347 | 1.83
2400 | 3162 | 891 | 1.03 | 935 | 1.1 | 980 | 1.17 | 1021 | 1.25 | 1062 | 1.33 | 1100 | 1.42 | 1167 | 1.6 | 1228 | 1.72 | 1286 | 1.86 | 1341 | 2 | 1393 | 2.16
2600 | 3426 | 959 | 1.3 | 999 | 1.38 | 1040 | 1.45 | 1081 | 1.53 | 1118 | 1.64 | 1156 | 1.71 | 1222 | 1.9 | 1282 | 2.07 | 1338 | 2.2 | 1390 | 2.36 | 1442 | 2.5
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-115
FC-115 · 15 in. Wheel Diameter · Tip Speed (FPM) = 3.93 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1200 | 894 | 281 | 0.07 | 350 | 0.1 | 415 | 0.16
1400 | 1043 | 300 | 0.1 | 362 | 0.13 | 420 | 0.19 | 479 | 0.21
1600 | 1192 | 319 | 0.13 | 380 | 0.17 | 440 | 0.21 | 484 | 0.26 | 538 | 0.3 | 582 | 0.35
1800 | 1341 | 340 | 0.17 | 403 | 0.21 | 460 | 0.24 | 489 | 0.32 | 545 | 0.36 | 589 | 0.41 | 675 | 0.54
2000 | 1490 | 360 | 0.21 | 425 | 0.27 | 475 | 0.27 | 510 | 0.35 | 560 | 0.43 | 594 | 0.48 | 678 | 0.6 | 755 | 0.72
2200 | 1639 | 382 | 0.27 | 440 | 0.33 | 498 | 0.41 | 540 | 0.39 | 580 | 0.52 | 618 | 0.57 | 683 | 0.69 | 758 | 0.8 | 825 | 0.95
2400 | 1788 | 408 | 0.34 | 460 | 0.41 | 517 | 0.49 | 562 | 0.56 | 600 | 0.62 | 630 | 0.68 | 688 | 0.8 | 762 | 0.92 | 830 | 1.06 | 890 | 1.21
2600 | 1937 | 430 | 0.43 | 480 | 0.5 | 536 | 0.58 | 580 | 0.66 | 620 | 0.73 | 650 | 0.81 | 718 | 0.92 | 767 | 1.05 | 834 | 1.2 | 896 | 1.34 | 956 | 1.51
2800 | 2086 | 458 | 0.54 | 502 | 0.6 | 556 | 0.69 | 599 | 0.77 | 639 | 0.86 | 670 | 0.94 | 736 | 1.08 | 772 | 1.2 | 850 | 1.35 | 901 | 1.52 | 958 | 1.7
3000 | 2235 | 482 | 0.64 | 525 | 0.72 | 576 | 0.8 | 619 | 0.9 | 652 | 0.99 | 693 | 1.08 | 752 | 1.22 | 804 | 1.36 | 860 | 1.52 | 912 | 1.7 | 963 | 1.89
3200 | 2385 | 510 | 0.77 | 550 | 0.84 | 597 | 0.93 | 638 | 1.03 | 674 | 1.13 | 712 | 1.23 | 772 | 1.41 | 828 | 1.54 | 875 | 1.71 | 928 | 1.9 | 968 | 2.02
3400 | 2534 | 538 | 0.92 | 570 | 1 | 619 | 1.08 | 658 | 1.18 | 692 | 1.27 | 731 | 1.39 | 795 | 1.6 | 848 | 1.74 | 894 | 1.95 | 940 | 2.16 | 980 | 2.25
3600 | 2683 | 570 | 1.1 | 595 | 1.17 | 642 | 1.25 | 679 | 1.35 | 715 | 1.37 | 750 | 1.59 | 813 | 1.62 | 866 | 1.99 | 900 | 2.26
3800 | 2832 | 600 | 1.27 | 625 | 1.26 | 665 | 1.44 | 700 | 1.53 | 736 | 1.62 | 770 | 1.8 | 832 | 1.9 | 880 | 2.36
4000 | 2981 | 632 | 1.5 | 650 | 1.52 | 689 | 1.65 | 723 | 1.75 | 756 | 1.92 | 790 | 2.1 | 851 | 2.23
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-118
FC-118 · 18 1/2 in. Wheel Diameter · Tip Speed (FPM) = 4.75 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
1600 | 990 | 278 | 0.12 | 340 | 0.18 | 386 | 0.21 | 420 | 0.23 | 457 | 0.27 | 495 | 0.31
1900 | 1176 | 306 | 0.19 | 364 | 0.24 | 412 | 0.29 | 450 | 0.33 | 484 | 0.38 | 513 | 0.41 | 572 | 0.49
2200 | 1361 | 338 | 0.26 | 389 | 0.33 | 436 | 0.4 | 476 | 0.46 | 510 | 0.51 | 540 | 0.55 | 593 | 0.64 | 642 | 0.72 | 700 | 0.85
2500 | 1547 | 369 | 0.37 | 416 | 0.44 | 459 | 0.52 | 500 | 0.59 | 535 | 0.66 | 566 | 0.72 | 621 | 0.82 | 667 | 0.92 | 710 | 1.01 | 756 | 1.13 | 809 | 1.28
2800 | 1733 | 402 | 0.41 | 445 | 0.55 | 485 | 0.65 | 523 | 0.75 | 560 | 0.83 | 591 | 0.92 | 646 | 1.03 | 694 | 1.14 | 737 | 1.25 | 775 | 1.36 | 812 | 1.47
3100 | 1918 | 437 | 0.64 | 476 | 0.73 | 512 | 0.83 | 548 | 0.92 | 583 | 1.02 | 615 | 1.12 | 671 | 1.28 | 719 | 1.41 | 763 | 1.54 | 803 | 1.66 | 838 | 1.78
3400 | 2104 | 473 | 0.91 | 508 | 0.97 | 542 | 1 | 575 | 1.12 | 607 | 1.23 | 638 | 1.34 | 696 | 1.55 | 745 | 1.71 | 788 | 1.86 | 828 | 2 | 866 | 2.13
3700 | 2290 | 510 | 1.19 | 538 | 0.99 | 573 | 1.22 | 603 | 1.36 | 634 | 1.48 | 663 | 1.59 | 720 | 1.83 | 770 | 2.05 | 814 | 2.23 | 854 | 2.38 | 891 | 2.54
4000 | 2475 | 546 | 1.48 | 573 | 1.21 | 605 | 1.57 | 633 | 1.6 | 661 | 1.77 | 690 | 1.89 | 743 | 2.14 | 794 | 2.4 | 840 | 2.63 | 880 | 2.81 | 917 | 2.99
4300 | 2661 | 583 | 1.77 | 608 | 1.66 | 636 | 1.89 | 664 | 1.92 | 690 | 2.06 | 717 | 2.23 | 768 | 2.48 | 817 | 2.77 | 864 | 3.05 | 905 | 3.27 | 943 | 3.48
4600 | 2847 | 619 | 2.06 | 644 | 2.19 | 667 | 1.82 | 696 | 2.39 | 721 | 2.39 | 745 | 2.58 | 795 | 2.88 | 841 | 3.17 | 887 | 3.48 | 929 | 3.75 | 968 | 4.01
4900 | 3032 | 655 | 2.36 | 680 | 2.74 | 701 | 2.23 | 727 | 2.85 | 752 | 2.85 | 775 | 2.94 | 822 | 3.33 | 866 | 3.61 | 910 | 3.94 | 932 | 4.26 | 992 | 4.55
5200 | 3218 | 691 | 2.65 | 716 | 3.3 | 736 | 2.9 | 758 | 2.82 | 784 | 3.46 | 806 | 3.4 | 846 | 3.8 | 893 | 4.12 | 934 | 4.44 | 975 | 4.77 | 1015 | 5.07
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-120
FC-120 · 20 in. Wheel Diameter · Tip Speed (FPM) = 5.24 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0" |  | 2-1/4" |  | 2-1/2" |  | 3.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
2500 | 902 | 230 | 0.17 | 289 | 0.25 | 334 | 0.31 | 371 | 0.36 | 415 | 0.45 | 460 | 0.55 | 543 | 0.78 | 614 | 1.01 | 678 | 1.25 | 737 | 1.49 | 790 | 1.79 | 837 | 2.02 | 881 | 2.29 | 963 | 2.87
3000 | 1083 | 252 | 0.26 | 305 | 0.35 | 353 | 0.42 | 390 | 0.5 | 421 | 0.58 | 455 | 0.66 | 528 | 0.88 | 602 | 1.13 | 667 | 1.4 | 726 | 1.68 | 781 | 1.96 | 832 | 2.25 | 881 | 2.55 | 967 | 3.16
3500 | 1263 | 276 | 0.38 | 324 | 0.47 | 368 | 0.56 | 408 | 0.67 | 442 | 0.76 | 470 | 0.84 | 525 | 1.02 | 587 | 1.26 | 652 | 1.55 | 715 | 1.86 | 769 | 2.17 | 821 | 2.48 | 870 | 2.81 | 960 | 3.48
4000 | 1444 | 301 | 0.54 | 346 | 0.63 | 386 | 0.74 | 423 | 0.86 | 459 | 0.98 | 491 | 1.09 | 542 | 1.28 | 587 | 1.46 | 643 | 1.73 | 697 | 2.02 | 755 | 2.37 | 809 | 2.71 | 859 | 3.08 | 949 | 3.8
4500 | 1624 | 327 | 0.7 | 368 | 0.84 | 406 | 0.97 | 441 | 1.09 | 474 | 1.2 | 507 | 1.34 | 562 | 1.59 | 607 | 1.81 | 647 | 2.01 | 695 | 2.29 | 743 | 2.6 | 791 | 2.93 | 843 | 3.32 | 938 | 4.12
5000 | 1805 | 355 | 0.97 | 392 | 1.08 | 428 | 1.23 | 460 | 1.35 | 492 | 1.5 | 522 | 1.64 | 579 | 1.92 | 628 | 2.19 | 668 | 2.45 | 705 | 2.68 | 743 | 2.92 | 788 | 3.27 | 831 | 3.61 | 921 | 4.4
5500 | 1985 | 383 | 1.22 | 418 | 1.41 | 451 | 1.52 | 482 | 1.68 | 511 | 1.81 | 540 | 1.99 | 594 | 2.3 | 642 | 2.61 | 689 | 2.9 | 725 | 3.19 | 760 | 3.44 | 793 | 3.69 | 831 | 4.01 | 909 | 4.77
6000 | 2166 | 412 | 1.65 | 444 | 1.73 | 474 | 1.89 | 504 | 2.08 | 532 | 2.22 | 559 | 2.37 | 611 | 2.72 | 659 | 3.05 | 705 | 3.4 | 746 | 3.72 | 780 | 4.02 | 813 | 4.32 | 843 | 4.6 | 909 | 5.25
6500 | 2346 | 442 | 2.16 | 470 | 2.11 | 499 | 2.35 | 527 | 2.49 | 554 | 2.69 | 580 | 2.85 | 629 | 3.2 | 675 | 3.56 | 721 | 3.93 | 762 | 4.3 | 800 | 4.62 | 833 | 5.02 | 864 | 5.32 | 921 | 5.92
7000 | 2527 | 471 | 2.69 | 498 | 2.65 | 525 | 2.85 | 551 | 2.98 | 577 | 3.19 | 602 | 3.4 | 648 | 3.73 | 694 | 4.15 | 735 | 4.51 | 777 | 4.95 | 816 | 5.32 | 852 | 5.72 | 885 | 6.09 | 941 | 6.79
7500 | 2707 | 501 | 3.2 | 526 | 3.17 | 551 | 3.86 | 577 | 3.61 | 600 | 3.78 | 624 | 3.99 | 670 | 4.39 | 712 | 4.74 | 754 | 5.22 | 793 | 5.62 | 832 | 6.05 | 868 | 6.48 | 902 | 6.9 | 962 | 7.7
8000 | 2888 | 530 | 3.71 | 554 | 3.69 | 578 | 3.97 | 603 | 4.29 | 625 | 4.49 | 647 | 4.64 | 691 | 5.11 | 732 | 5.5 | 772 | 5.92 | 810 | 6.42 | 847 | 6.83 | 883 | 7.31 | 918 | 7.72 | 981 | 8.65
8500 | 3068 | 559 | 4.25 | 584 | 4.69 | 607 | 4.74 | 628 | 4.95 | 650 | 5.25 | 671 | 5.36 | 714 | 5.88 | 753 | 6.32 | 791 | 6.7 | 828 | 7.24 | 864 | 7.75 | 898 | 8.18 | 933 | 8.68 | 997 | 9.62
9000 | 3249 | 591 | 4.75 | 613 | 5.73 | 635 | 5.53 | 654 | 5.61 | 676 | 6.08 | 697 | 6.29 | 736 | 6.69 | 776 | 7.23 | 812 | 7.7 | 846 | 8.05 | 882 | 8.68 | 916 | 9.22 | 948 | 9.68 | 1013 | 10.7
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-122
FC-122 · 22 in. Wheel Diameter · Tip Speed (FPM) = 5.76 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0" |  | 2-1/2" |  | 3.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3000 | 959 | 207 | 0.19 | 254 | 0.26 | 292 | 0.33 | 328 | 0.4 | 365 | 0.48
3500 | 1119 | 225 | 0.27 | 269 | 0.35 | 306 | 0.43 | 338 | 0.51 | 369 | 0.6 | 400 | 0.68
4000 | 1279 | 244 | 0.38 | 284 | 0.47 | 321 | 0.56 | 352 | 0.65 | 380 | 0.74 | 407 | 0.84 | 462 | 1.04
4500 | 1439 | 264 | 0.51 | 302 | 0.62 | 335 | 0.72 | 367 | 0.82 | 395 | 0.92 | 420 | 1.02 | 468 | 1.24 | 517 | 1.46
5000 | 1598 | 285 | 0.67 | 320 | 0.8 | 351 | 0.91 | 381 | 1.03 | 410 | 1.13 | 435 | 1.24 | 479 | 1.47 | 523 | 1.71 | 566 | 1.96 | 611 | 2.23
5500 | 1758 | 307 | 0.87 | 339 | 1 | 369 | 1.13 | 396 | 1.26 | 424 | 1.38 | 449 | 1.5 | 494 | 1.74 | 534 | 2 | 573 | 2.26 | 612 | 2.52 | 653 | 2.82
6000 | 1918 | 328 | 1.1 | 359 | 1.25 | 387 | 1.39 | 414 | 1.53 | 438 | 1.67 | 464 | 1.8 | 508 | 2.07 | 548 | 2.33 | 584 | 2.61 | 620 | 2.9 | 656 | 3.18 | 730 | 3.82
6500 | 2078 | 351 | 1.37 | 379 | 1.53 | 406 | 1.69 | 431 | 1.84 | 455 | 1.99 | 478 | 2.14 | 523 | 2.43 | 562 | 2.71 | 598 | 3 | 631 | 3.31 | 664 | 3.61 | 731 | 4.25 | 800 | 4.97
7000 | 2238 | 373 | 1.68 | 400 | 1.86 | 425 | 2.03 | 450 | 2.2 | 473 | 2.36 | 495 | 2.52 | 537 | 2.84 | 577 | 3.15 | 612 | 3.45 | 645 | 3.77 | 676 | 4.09 | 738 | 4.76 | 801 | 5.46
7500 | 2398 | 397 | 2.04 | 421 | 2.23 | 446 | 2.42 | 469 | 2.6 | 491 | 2.77 | 512 | 2.95 | 552 | 3.29 | 592 | 3.62 | 627 | 3.95 | 660 | 4.27 | 690 | 4.62 | 747 | 5.31 | 806 | 6.04
8000 | 2558 | 421 | 2.46 | 443 | 2.65 | 466 | 2.85 | 488 | 3.05 | 509 | 3.24 | 530 | 3.42 | 568 | 3.79 | 606 | 4.16 | 642 | 4.5 | 674 | 4.86 | 705 | 5.2 | 761 | 5.94 | 814 | 6.69
8500 | 2717 | 444 | 2.94 | 465 | 3.12 | 487 | 3.34 | 508 | 3.55 | 528 | 3.76 | 548 | 3.96 | 585 | 4.35 | 620 | 4.73 | 656 | 5.12 | 689 | 5.49 | 719 | 5.86 | 775 | 6.61 | 826 | 7.41
9000 | 2877 | 468 | 3.47 | 487 | 3.64 | 508 | 3.88 | 528 | 4.11 | 548 | 4.33 | 567 | 4.54 | 603 | 4.95 | 637 | 5.37 | 670 | 5.78 | 704 | 6.18 | 734 | 6.58 | 790 | 7.35 | 840 | 8.19
9500 | 3037 | 493 | 4.06 | 510 | 4.23 | 530 | 4.48 | 549 | 4.72 | 568 | 4.96 | 586 | 5.19 | 621 | 5.63 | 654 | 6.07 | 686 | 6.5 | 718 | 6.94 | 749 | 7.35
10000 | 3197 | 517 | 4.72 | 532 | 4.88 | 552 | 5.14 | 570 | 5.39 | 588 | 5.65 | 606 | 5.89 | 640 | 6.37 | 672 | 6.82 | 703 | 7.29
10500 | 3357 | 541 | 5.44 | 556 | 5.62 | 574 | 5.87 | 591 | 6.14 | 609 | 6.4 | 626 | 6.67 | 659 | 7.17
11000 | 3517 | 565 | 6.24 | 580 | 6.42 | 596 | 6.66 | 613 | 6.95 | 630 | 7.22 | 646 | 7.51
11500 | 3676 | 590 | 7.11 | 604 | 7.3 | 618 | 7.52
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-126
FC-126 · 26 in. Wheel Diameter · Tip Speed (FPM) = 6.80 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0" |  | 2-1/2" |  | 3.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
3000 | 691 | 153 | 0.13 | 197 | 0.2 | 240 | 0.29
4000 | 922 | 171 | 0.24 | 212 | 0.33 | 244 | 0.42 | 277 | 0.52 | 309 | 0.64
5000 | 1152 | 193 | 0.41 | 229 | 0.52 | 261 | 0.63 | 288 | 0.74 | 313 | 0.86 | 339 | 0.98 | 392 | 1.27
6000 | 1382 | 217 | 0.64 | 249 | 0.78 | 279 | 0.91 | 306 | 1.05 | 329 | 1.18 | 351 | 1.32 | 393 | 1.6 | 437 | 1.92
7000 | 1613 | 242 | 0.95 | 271 | 1.12 | 298 | 1.28 | 323 | 1.44 | 347 | 1.59 | 368 | 1.74 | 406 | 2.07 | 442 | 2.4 | 479 | 2.74 | 517 | 3.12
8000 | 1843 | 268 | 1.35 | 294 | 1.55 | 319 | 1.74 | 342 | 1.93 | 364 | 2.11 | 386 | 2.28 | 423 | 2.63 | 457 | 3 | 488 | 3.37 | 521 | 3.76 | 553 | 4.16
9000 | 2074 | 295 | 1.86 | 319 | 2.09 | 342 | 2.31 | 363 | 2.52 | 384 | 2.73 | 403 | 2.93 | 441 | 3.33 | 474 | 3.72 | 505 | 4.13 | 533 | 4.55 | 561 | 4.98 | 619 | 5.86 | 677 | 6.87
10000 | 2304 | 322 | 2.5 | 344 | 2.75 | 365 | 3 | 386 | 3.24 | 405 | 3.47 | 423 | 3.7 | 459 | 4.16 | 492 | 4.6 | 522 | 5.03 | 550 | 3.48 | 576 | 5.95 | 527 | 6.89 | 678 | 7.85
11000 | 2535 | 351 | 3.29 | 370 | 3.55 | 390 | 3.83 | 409 | 4.09 | 427 | 4.36 | 444 | 4.6 | 477 | 5.11 | 510 | 5.61 | 540 | 6.09 | 568 | 6.58 | 593 | 7.04 | 641 | 8.08 | 687 | 9.12
12000 | 2765 | 380 | 4.23 | 397 | 4.49 | 415 | 4.79 | 433 | 5.1 | 450 | 5.38 | 467 | 5.67 | 498 | 6.22 | 527 | 6.76 | 557 | 7.32 | 586 | 7.83 | 611 | 8.37 | 658 | 9.42 | 701 | 10.5
13000 | 2995 | 409 | 5.34 | 424 | 5.58 | 441 | 5.92 | 458 | 6.25 | 474 | 6.58 | 489 | 6.89 | 520 | 7.49 | 548 | 8.1 | 575 | 8.68 | 603 | 9.28 | 629 | 9.83
14000 | 3226 | 438 | 6.64 | 451 | 6.86 | 468 | 7.23 | 483 | 7.58 | 499 | 7.94 | 513 | 8.28 | 542 | 8.95 | 569 | 9.58
15000 | 3456 | 468 | 8.12 | 480 | 8.37 | 494 | 8.71 | 509 | 9.1 | 524 | 9.48 | 538 | 9.86
16000 | 3687 | 497 | 9.82 | 509 | 10.1
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## FC-130
FC-130 · 30 1/4 in. Wheel Diameter · Tip Speed (FPM) = 7.92 × RPM
VOLUME CFM | O.V. FPM | STATIC PRESSURE — in. WG
|  | 1/8" |  | 1/4" |  | 3/8" |  | 1/2" |  | 5/8" |  | 3/4" |  | 1.0" |  | 1-1/4" |  | 1-1/2" |  | 1-3/4" |  | 2.0" |  | 2-1/2" |  | 3.0"
|  | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP | RPM | BHP
6000 | 1050 | 159 | 0.41 | 194 | 0.56 | 226 | 0.71 | 249 | 0.84 | 266 | 0.94 | 285 | 1.1
7000 | 1225 | 175 | 0.61 | 207 | 0.77 | 239 | 0.97 | 267 | 1.12 | 285 | 1.3 | 299 | 1.4 | 337 | 1.8
8000 | 1400 | 184 | 0.81 | 221 | 1.04 | 252 | 1.29 | 276 | 1.48 | 302 | 1.69 | 320 | 1.89 | 346 | 2.13 | 381 | 2.6 | 410 | 3.02 | 435 | 3.41
9000 | 1575 | 198 | 1.08 | 231 | 1.32 | 264 | 1.63 | 285 | 1.83 | 309 | 2.07 | 330 | 2.42 | 362 | 2.7 | 389 | 3.08 | 414 | 3.48 | 439 | 3.83
10000 | 1750 | 213 | 1.44 | 244 | 1.7 | 274 | 2 | 294 | 2.24 | 317 | 2.53 | 338 | 2.81 | 379 | 3.32 | 406 | 3.81 | 428 | 4.09 | 448 | 4.53 | 473 | 5.05
11000 | 1925 | 229 | 1.88 | 257 | 2.11 | 282 | 2.43 | 307 | 2.74 | 328 | 3.04 | 348 | 3.35 | 391 | 3.97 | 419 | 4.42 | 444 | 4.93 | 468 | 5.36 | 484 | 5.82 | 527 | 6.85 | 568 | 7.86
12000 | 2100 | 246 | 2.27 | 270 | 2.65 | 296 | 2.98 | 320 | 3.32 | 337 | 3.61 | 349 | 3.78 | 395 | 4.67 | 430 | 5.27 | 455 | 5.83 | 481 | 6.36 | 497 | 7.26 | 539 | 7.72 | 575 | 8.9
13000 | 2275 | 269 | 2.96 | 284 | 3.28 | 310 | 3.61 | 333 | 3.95 | 349 | 4.28 | 367 | 4.61 | 404 | 5.39 | 443 | 6.23 | 468 | 6.41 | 493 | 7.29 | 509 | 7.93 | 553 | 8.99 | 584 | 9.97
14000 | 2450 | 289 | 3.6 | 304 | 3.92 | 323 | 4.36 | 345 | 4.73 | 365 | 5.11 | 384 | 5.29 | 413 | 6.19 | 444 | 6.92 | 481 | 7.8 | 507 | 8.54 | 531 | 9.11 | 571 | 10.49 | 599 | 11.24
15000 | 2625 | 306 | 4.41 | 326 | 4.82 | 337 | 5.08 | 359 | 5.58 | 381 | 6 | 401 | 6.56 | 429 | 7.19 | 461 | 8.2 | 488 | 8.9 | 515 | 9.6 | 545 | 10.65 | 585 | 11.9 | 612 | 12.9
16000 | 2800 | 320 | 5.26 | 337 | 5.61 | 357 | 6.09 | 370 | 6.52 | 393 | 7.04 | 406 | 7.39 | 438 | 8.22 | 467 | 9.15 | 498 | 10 | 527 | 11 | 552 | 11.8 | 604 | 13.58 | 627 | 14.28
17000 | 2975 | 343 | 6.39 | 354 | 6.66 | 372 | 7.29 | 385 | 7.59 | 402 | 8.04 | 418 | 8.47 | 452 | 9.51 | 481 | 10.31 | 515 | 11.53 | 533 | 12.2 | 564 | 13.33 | 618 | 15.27 | 645 | 16.31
18000 | 3150 | 364 | 7.62 | 374 | 7.84 | 393 | 8.42 | 399 | 8.52 | 413 | 9 | 435 | 9.77 | 466 | 10.62 | 491 | 11.59 | 520 | 12.66 | 543 | 13.66 | 569 | 14.69 | 621 | 16.81 | 655 | 18.18
19000 | 3325 | 379 | 8.77 | 392 | 9.11 | 404 | 9.54 | 418 | 9.95 | 429 | 10.39 | 447 | 11.16 | 483 | 12.5 | 507 | 13.2 | 533 | 14.45 | 559 | 15.4 | 582 | 16.35 | 633 | 18.85 | 658 | 19.8
20000 | 3500 | 400 | 10.2 | 408 | 10.46 | 421 | 10.94 | 428 | 11.19 | 449 | 11.98 | 468 | 12.71 | 492 | 13.7 | 519 | 14.89 | 546 | 15.9 | 563 | 16.76 | 602 | 18.53
21000 | 3675 | 416 | 11.58 | 426 | 12.11 | 440 | 12.65 | 452 | 13.24 | 469 | 13.8 | 481 | 14.29 | 501 | 15.27 | 530 | 16.62 | 564 | 18.19 | 577 | 18.79
22000 | 3850 | 436 | 13.36 | 444 | 13.85 | 463 | 14.59 | 469 | 14.94 | 494 | 16.04 | 500 | 16.21 | 509 | 16.67 | 543 | 18.4
Performance is for Type B — Free Inlet, Ducted Outlet. BHP excludes drive (belt) losses. Ratings do not include the effects of appurtenances in the airstream. Blank cells = not rated at that SP/CFM.

## Source Notes
Source Notes & Flagged Values
All values transcribed exactly as printed in the source catalog (pages 5-7). The cells below look inconsistent with their neighbours and are most likely typos in the original PDF — verify against the printed catalog before using them in AeroQuote.
Model | CFM | SP (in. WG) | Note
FC-126 | 10000 | 1-3/4" | BHP 3.48 breaks the trend (neighbors 5.03 and 5.95) — likely a source typo.
FC-126 | 10000 | 2-1/2" | RPM 527 is lower than the 2.0" value (576) — likely a source typo.
FC-118 | 4600 | 3/8" | BHP 1.82 is out of sequence vs neighbors — printed as-is in catalog.
FC-118 | 4900 | 3/8" | BHP 2.23 is out of sequence vs neighbors — printed as-is in catalog.
FC-118 | 5200 | 1/2" | RPM 758 / BHP 2.82 dips below the 3/8" entry — printed as-is in catalog.